## Start Here
Topic | Read before using
Source | MITRE ATT&CK® for ICS v19.2. Source content under MITRE's license; see License sheet. Independent reference, not endorsed by MITRE.
Views | Four platform views filter the full ICS matrix. Missing from a view does not mean not applicable. These are not the Enterprise platform matrices.
Membership | Website-rule membership uses direct platform tags AND parent visibility. Available archive pages are verified; unavailable historical platform pages are explicitly derived, NOT observed website snapshots. See Provenance. Raw tags are retained separately, including literal None and absent fields.
Counts | Unique technique IDs count parents and children separately. A technique may appear in multiple tactics. Counts/colors do not measure risk, coverage, maturity or compliance.
Assets | Asset role and OS are separate. Classify each controller, workstation, server and appliance. Do not assume a controller runs Linux or that COTS means Windows.
Safety | No installed environment has been assessed. This reference authorizes no scanning or testing. Coordinate live-system validation with operations, safety and vendors.
History | A release is a reference snapshot, not the date an adversary first used a behavior. Revoked/deprecated objects remain in the source ZIP and JSON export.
Provenance | Source SHA-256: 08b83d2cea6b6d6752468ef0e62e2ab2a53c9443ef72c439ecccb07ab9e89da9

## ICS Matrix
Initial Access TA0108 | Execution TA0104 | Persistence TA0110 | Privilege Escalation TA0111 | Evasion TA0103 | Discovery TA0102 | Lateral Movement TA0109 | Collection TA0100 | Command and Control TA0101 | Inhibit Response Function TA0107 | Impair Process Control TA0106 | Impact TA0105
T0817 Drive-by Compromise | T0895 Autorun Image | T1694 Insecure Credentials | T0890 Exploitation for Privilege Escalation | T0858 Change Operating Mode | T0840 Network Connection Enumeration | T0866 Exploitation of Remote Services | T0830 Adversary-in-the-Middle | T0885 Commonly Used Port | T0800 Activate Firmware Update Mode | T0806 Brute Force I/O | T0879 Damage to Property
T0819 Exploit Public-Facing Application | T0858 Change Operating Mode | ↳ T1694.001 Default Credentials | T0874 Hooking | T0820 Exploitation for Evasion | T0842 Network Sniffing | T1694 Insecure Credentials | T0802 Automated Collection | T0884 Connection Proxy | T0878 Alarm Suppression | T1693 Modify Firmware | T0813 Denial of Control
T0866 Exploitation of Remote Services | T0807 Command-Line Interface | ↳ T1694.002 Hardcoded Credentials |  | T0872 Indicator Removal on Host | T0846 Remote System Discovery | ↳ T1694.001 Default Credentials | T0811 Data from Information Repositories | T0869 Standard Application Layer Protocol | T1695 Block Communications | ↳ T1693.001 System Firmware | T0815 Denial of View
T0822 External Remote Services | T0871 Execution through API | T1693 Modify Firmware |  | T0849 Masquerading | ↳ T0846.001 Port Scan | ↳ T1694.002 Hardcoded Credentials | T0893 Data from Local System |  | ↳ T1695.001 Serial COM | ↳ T1693.002 Module Firmware | T0826 Loss of Availability
T0883 Internet Accessible Device | T0823 Graphical User Interface | ↳ T1693.001 System Firmware |  | T0851 Rootkit | ↳ T0846.002 Broadcast Discovery | T0867 Lateral Tool Transfer | T0868 Detect Operating Mode |  | ↳ T1695.002 Ethernet | T0836 Modify Parameter | T0827 Loss of Control
T0886 Remote Services | T0874 Hooking | ↳ T1693.002 Module Firmware |  | T0894 System Binary Proxy Execution | ↳ T0846.003 Multicast Discovery | T0843 Program Download | T0877 I/O Image |  | ↳ T1695.003 Wi-Fi | T1692 Unauthorized Message | T0828 Loss of Productivity and Revenue
T0847 Replication Through Removable Media | T0821 Modify Controller Tasking | T0889 Modify Program |  | T1692 Unauthorized Message | T0888 Remote System Information Discovery | ↳ T0843.001 Download All | T0801 Monitor Process State |  | T1691 Block Operational Technology Message | ↳ T1692.001 Command Message | T0837 Loss of Protection
T0848 Rogue Master | T0834 Native API | T0873 Project File Infection |  | ↳ T1692.001 Command Message | T0887 Wireless Sniffing | ↳ T0843.002 Online Edit | T0861 Point & Tag Identification |  | ↳ T1691.001 Command Message | ↳ T1692.002 Reporting Message | T0880 Loss of Safety
T0865 Spearphishing Attachment | T0853 Scripting | ↳ T0873.001 Siemens Project File Format |  | ↳ T1692.002 Reporting Message |  | ↳ T0843.003 Program Append | T0845 Program Upload |  | ↳ T1691.002 Reporting Message |  | T0829 Loss of View
T0862 Supply Chain Compromise | T0863 User Execution | T0859 Valid Accounts |  |  |  | T0886 Remote Services | T0852 Screen Capture |  | T0892 Change Credential |  | T0831 Manipulation of Control
T0864 Transient Cyber Asset | [5 empty] | T0859 Valid Accounts | T0887 Wireless Sniffing |  | T0809 Data Destruction |  | T0832 Manipulation of View
T0860 Wireless Compromise | [8 empty] | T0814 Denial of Service |  | T0882 Theft of Operational Information
T0816 Device Restart/Shutdown
T0835 Manipulate I/O Image
T0838 Modify Alarm Settings
T1693 Modify Firmware
↳ T1693.001 System Firmware
↳ T1693.002 Module Firmware
T0851 Rootkit
T0881 Service Stop
Note on A2: Adversaries may gain access to a system during a drive-by compromise, when a user visits a website as part of a regular browsing session. With this technique, the user's web browser is targeted and exploited simply by visiting the compromised website. The adversary may target a specific community, such as trusted third party suppliers or other industry specific groups, which often visit the target website. This kind of targeted attack relies on a common interest, and is known as a strategic web compromise or watering hole attack. The National Cyber Awareness System (NCAS) has issued a Technical Alert (TA) regarding Russian government cyber activity targeting critical infrastructure sectors. (Citation: Cybersecurity & Infrastructure Security Agency March 2018) Analysis by DHS and FBI has noted two distinct categories of victims in the Dragonfly campaign on the Western energy sector: staging and intended targets. The adversary targeted the less secure networks of staging targets, including trusted third-party suppliers and related peripheral organizations. Initial access to the intended targets used watering hole attacks to target process control, ICS, and critical infrastructure related trade publications and informational websites. MITRE source; not an assessment.
Note on B2: Adversaries may leverage AutoRun functionality or scripts to execute malicious code. Devices configured to enable AutoRun functionality or legacy operating systems may be susceptible to abuse of these features to run malicious code stored on various forms of removeable media (i.e., USB, Disk Images [.ISO]). Commonly, AutoRun or AutoPlay are disabled in many operating systems configurations to mitigate against this technique. If a device is configured to enable AutoRun or AutoPlay, adversaries may execute code on the device by mounting the removable media to the device, either through physical or virtual means. This may be especially relevant for virtual machine environments where disk images may be dynamically mapped to a guest system on a hypervisor. An example could include an adversary gaining access to a hypervisor through the management interface to modify a virtual machine’s hardware configuration. They could then deploy an iso image with a malicious AutoRun script to cause the virtual machine to automatically execute the code contained on the disk image. This would enable the execution of malicious code within a virtual machine without needing any prior remote access to that system. MITRE source; not an assessment.
Note on C2: Adversaries may target insecure credentials as a means to persist on a system or device or move laterally from one system or device to another. Insecure credentials may appear as default credentials which are pre-configured credentials on a system, device, or software that are well-known in documentation or hard-coded credentials which are built into the system, device, or software that cannot be changed or not easily changed because of the impact on control processes.(Citation: NIST SP 800-82r3)(Citation: ICS-ALERT-13-164-01)(Citation: OT IceFall) Adversaries often times use insecure credentials to evade detection as they are typically forgotten about by system and device owners. MITRE source; not an assessment.
Note on D2: Adversaries may exploit software vulnerabilities in an attempt to elevate privileges. Exploitation of a software vulnerability occurs when an adversary takes advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Security constructs such as permission levels will often hinder access to information and use of certain techniques, so adversaries will likely need to perform privilege escalation to include use of software exploitation to circumvent those restrictions. (Citation: The MITRE Corporation) When initially gaining access to a system, an adversary may be operating within a lower privileged process which will prevent them from accessing certain resources on the system. Vulnerabilities may exist, usually in operating system components and software commonly running at higher permissions, that can be exploited to gain higher levels of access on the system. This could enable someone to move from unprivileged or user level permissions to SYSTEM or root permissions depending on the component that is vulnerable. This may be a necessary step for an adversary compromising an endpoint system that has been properly configured and limits other privilege escalation methods. (Citation: The MITRE Corporation) MITRE source; not an assessment.
Note on E2: Adversaries may change the operating mode of a controller to gain additional access to engineering functions such as Program Download. Programmable controllers typically have several modes of operation that control the state of the user program and control access to the controllers API. Operating modes can be physically selected using a key switch on the face of the controller but may also be selected with calls to the controllers API. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: * Program - This mode must be enabled before changes can be made to a devices program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLCs logic Is halted, and all outputs may be forced off. (Citation: N.A. October 2017) * Run - Execution of the devices program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the programs logic. Program Upload and Program Download are disabled while in this mode. (Citation: Omron) (Citation: Machine Information Systems 2007) (Citation: N.A. October 2017) (Citation: PLCgurus 2021) * Remote - Allows for remote changes to a PLCs operation mode. (Citation: PLCgurus 2021) * Stop - The PLC and program is stopped, while in this mode, outputs are forced off. (Citation: Machine Information Systems 2007) * Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. (Citation: Machine Information Systems 2007) * Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. (Citation: Omron) MITRE source; not an assessment.
Note on F2: Adversaries may perform network connection enumeration to discover information about device communication patterns. If an adversary can inspect the state of a network connection with tools, such as Netstat(Citation: Netstat), in conjunction with System Firmware, then they can determine the role of certain devices on the network (Citation: MITRE). The adversary can also use Network Sniffing to watch network traffic for details about the source, destination, protocol, and content. MITRE source; not an assessment.
Note on G2: Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to enable remote service abuse. A common goal for post-compromise exploitation of remote services is for initial access into and lateral movement throughout the ICS environment to enable access to targeted systems. (Citation: Enterprise ATT&CK) ICS asset owners and operators have been affected by ransomware (or disruptive malware masquerading as ransomware) migrating from enterprise IT to ICS environments: WannaCry, NotPetya, and BadRabbit. In each of these cases, self-propagating (wormable) malware initially infected IT networks, but through exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks, producing significant impacts. (Citation: Joe Slowik April 2019) MITRE source; not an assessment.
Note on H2: Adversaries with privileged network access may seek to modify network traffic in real time using adversary-in-the-middle (AiTM) attacks. (Citation: Gabriel Sanchez October 2017) This type of attack allows the adversary to intercept traffic to and/or from a particular device on the network. If a AiTM attack is established, then the adversary has the ability to block, log, modify, or inject traffic into the communication stream. There are several ways to accomplish this attack, but some of the most-common are Address Resolution Protocol (ARP) poisoning and the use of a proxy. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) An AiTM attack may allow an adversary to perform the following attacks: Block Reporting Message, Spoof Reporting Message, Modify Parameter, Unauthorized Command Message MITRE source; not an assessment.
Note on I2: Adversaries may communicate over a commonly used port to bypass firewalls or network detection systems and to blend in with normal network activity, to avoid more detailed inspection. They may use the protocol associated with the port, or a completely different protocol. They may use commonly open ports, such as the examples provided below. * TCP:80 (HTTP) * TCP:443 (HTTPS) * TCP/UDP:53 (DNS) * TCP:1024-4999 (OPC on XP/Win2k3) * TCP:49152-65535 (OPC on Vista and later) * TCP:23 (TELNET) * UDP:161 (SNMP) * TCP:502 (MODBUS) * TCP:102 (S7comm/ISO-TSAP) * TCP:20000 (DNP3) * TCP:44818 (Ethernet/IP) MITRE source; not an assessment.
Note on J2: Adversaries may activate firmware update mode on devices to prevent expected response functions from engaging in reaction to an emergency or process malfunction. For example, devices such as protection relays may have an operation mode designed for firmware installation. This mode may halt process monitoring and related functions to allow new firmware to be loaded. A device left in update mode may be placed in an inactive holding state if no firmware is provided to it. By entering and leaving a device in this mode, the adversary may deny its usual functionalities. MITRE source; not an assessment.
Note on K2: Adversaries may repetitively or successively change I/O point values to perform an action. Brute Force I/O may be achieved by changing either a range of I/O point values or a single point value repeatedly to manipulate a process function. The adversary's goal and the information they have about the target environment will influence which of the options they choose. In the case of brute forcing a range of point values, the adversary may be able to achieve an impact without targeting a specific point. In the case where a single point is targeted, the adversary may be able to generate instability on the process function associated with that particular point. Adversaries may use Brute Force I/O to cause failures within various industrial processes. These failures could be the result of wear on equipment or damage to downstream equipment. MITRE source; not an assessment.
Note on L2: Adversaries may cause damage and destruction of property to infrastructure, equipment, and the surrounding environment when attacking control systems. This technique may result in device and operational equipment breakdown, or represent tangential damage from other techniques used in an attack. Depending on the severity of physical damage and disruption caused to control processes and systems, this technique may result in Loss of Safety. Operations that result in Loss of Control may also cause damage to property, which may be directly or indirectly motivated by an adversary seeking to cause impact in the form of Loss of Productivity and Revenue. The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill under an incidents affecting business section of its 2014 IT Security Report. (Citation: BSI State of IT Security 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact and damage resulted from the uncontrolled shutdown of a blast furnace. A Polish student used a remote controller device to interface with the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) (Citation: Bruce Schneier January 2008) Using this remote, the student was able to capture and replay legitimate tram signals. This resulted in damage to impacted trams, people, and the surrounding property. Reportedly, four trams were derailed and were forced to make emergency stops. (Citation: Shelley Smith February 2008) Commands issued by the student may have also resulted in tram collisions, causing harm to those on board and the environment outside. (Citation: Bruce Schneier January 2008) MITRE source; not an assessment.
Note on A3: Adversaries may leverage weaknesses to exploit internet-facing software for initial access into an industrial network. Internet-facing software may be user applications, underlying networking implementations, an assets operating system, weak defenses, etc. Targets of this technique may be intentionally exposed for the purpose of remote management and visibility. An adversary may seek to target public-facing applications as they may provide direct access into an ICS environment or the ability to move into the ICS network. Publicly exposed applications may be found through online tools that scan the internet for open ports and services. Version numbers for the exposed application may provide adversaries an ability to target specific known vulnerabilities. Exposed control protocol or remote access ports found in Commonly Used Port may be of interest by adversaries. MITRE source; not an assessment.
Note on B3: Adversaries may change the operating mode of a controller to gain additional access to engineering functions such as Program Download. Programmable controllers typically have several modes of operation that control the state of the user program and control access to the controllers API. Operating modes can be physically selected using a key switch on the face of the controller but may also be selected with calls to the controllers API. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: * Program - This mode must be enabled before changes can be made to a devices program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLCs logic Is halted, and all outputs may be forced off. (Citation: N.A. October 2017) * Run - Execution of the devices program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the programs logic. Program Upload and Program Download are disabled while in this mode. (Citation: Omron) (Citation: Machine Information Systems 2007) (Citation: N.A. October 2017) (Citation: PLCgurus 2021) * Remote - Allows for remote changes to a PLCs operation mode. (Citation: PLCgurus 2021) * Stop - The PLC and program is stopped, while in this mode, outputs are forced off. (Citation: Machine Information Systems 2007) * Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. (Citation: Machine Information Systems 2007) * Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. (Citation: Omron) MITRE source; not an assessment.
Note on C3: Adversaries may leverage manufacturer or supplier set default credentials on control system devices. These default credentials may have administrative permissions and may be necessary for initial configuration of the device. It is general best practice to change the passwords for these accounts as soon as possible, but some manufacturers may have devices that have passwords or usernames that cannot be changed.(Citation: Keith Stouffer May 2015) Default credentials are normally documented in an instruction manual that is either packaged with the device, published online through official means, or published online through unofficial means. Adversaries may leverage default credentials that have not been properly modified or disabled. MITRE source; not an assessment.
Note on D3: Adversaries may hook into application programming interface (API) functions used by processes to redirect calls for execution and privilege escalation means. Windows processes often leverage these API functions to perform tasks that require reusable system resources. Windows API functions are typically stored in dynamic-link libraries (DLLs) as exported functions. (Citation: Enterprise ATT&CK) One type of hooking seen in ICS involves redirecting calls to these functions via import address table (IAT) hooking. IAT hooking uses modifications to a process IAT, where pointers to imported API functions are stored. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) MITRE source; not an assessment.
Note on E3: Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to evade detection. Vulnerabilities may exist in software that can be used to disable or circumvent security features. Adversaries may have prior knowledge through Remote System Information Discovery about security features implemented on control devices. These device security features will likely be targeted directly for exploitation. There are examples of firmware RAM/ROM consistency checks on control devices being targeted by adversaries to enable the installation of malicious System Firmware. MITRE source; not an assessment.
Note on F3: Network sniffing is the practice of using a network interface on a computer system to monitor or capture information (Citation: Enterprise ATT&CK January 2018) regardless of whether it is the specified destination for the information. An adversary may attempt to sniff the traffic to gain information about the target. This information can vary in the level of importance. Relatively unimportant information is general communications to and from machines. Relatively important information would be login information. User credentials may be sent over an unencrypted protocol, such as Telnet, that can be captured and obtained through network packet analysis. In addition, ARP and Domain Name Service (DNS) poisoning can be used to capture credentials to websites, proxies, and internal systems by redirecting traffic to an adversary. MITRE source; not an assessment.
Note on G3: Adversaries may target insecure credentials as a means to persist on a system or device or move laterally from one system or device to another. Insecure credentials may appear as default credentials which are pre-configured credentials on a system, device, or software that are well-known in documentation or hard-coded credentials which are built into the system, device, or software that cannot be changed or not easily changed because of the impact on control processes.(Citation: NIST SP 800-82r3)(Citation: ICS-ALERT-13-164-01)(Citation: OT IceFall) Adversaries often times use insecure credentials to evade detection as they are typically forgotten about by system and device owners. MITRE source; not an assessment.
Note on H3: Adversaries may automate collection of industrial environment information using tools or scripts. This automated collection may leverage native control protocols and tools available in the control systems environment. For example, the OPC protocol may be used to enumerate and gather information. Access to a system or interface with these native protocols may allow collection and enumeration of other attached, communicating servers and devices. MITRE source; not an assessment.
Note on I3: Adversaries may use a connection proxy to direct network traffic between systems or act as an intermediary for network communications. The definition of a proxy can also be expanded to encompass trust relationships between networks in peer-to-peer, mesh, or trusted connections between networks consisting of hosts or systems that regularly communicate with each other. The network may be within a single organization or across multiple organizations with trust relationships. Adversaries could use these types of relationships to manage command and control communications, to reduce the number of simultaneous outbound network connections, to provide resiliency in the face of connection loss, or to ride over existing trusted communications paths between victims to avoid suspicion. (Citation: Enterprise ATT&CK January 2018) MITRE source; not an assessment.
Note on J3: Adversaries may target protection function alarms to prevent them from notifying operators of critical conditions. Alarm messages may be a part of an overall reporting system and of particular interest for adversaries. Disruption of the alarm system does not imply the disruption of the reporting system as a whole. A Secura presentation on targeting OT notes a dual fold goal for adversaries attempting alarm suppression: prevent outgoing alarms from being raised and prevent incoming alarms from being responded to. (Citation: Jos Wetzels, Marina Krotofil 2019) The method of suppression may greatly depend on the type of alarm in question: * An alarm raised by a protocol message * An alarm signaled with I/O * An alarm bit set in a flag (and read) In ICS environments, the adversary may have to suppress or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: Jos Wetzels, Marina Krotofil 2019) Methods of suppression may involve tampering or altering device displays and logs, modifying in memory code to fixed values, or even tampering with assembly level instruction code. MITRE source; not an assessment.
Note on K3: Firmware is low-level software embedded in hardware that enables systems and devices to function properly and is commonly found in ICS environments. Adversaries may modify firmware on a system or device by installing malicious or vulnerable versions that enable them to achieve objectives such as Persistence, Impair Process Control, and Inhibit Response Function. Adversaries may modify system and device firmware by using the built-in firmware update functionality which may support local or remote installation. The malicious or vulnerable firmware may be delivered via Replication Through Removable Media, Supply Chain Compromise, or Remote Services. Once installed, the malicious or vulnerable firmware could be used to provide Rootkit and Hooking functionality, Exploitation for Privilege Escalation, or Denial of Service.(Citation: Basnight, Zachry, et al.) MITRE source; not an assessment.
Note on L3: Adversaries may cause a denial of control to temporarily prevent operators and engineers from interacting with process controls. An adversary may attempt to deny process control access to cause a temporary loss of communication with the control device or to prevent operator adjustment of process controls. An affected process may still be operating during the period of control loss, but not necessarily in a desired state. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) In the 2017 Dallas Siren incident operators were unable to disable the false alarms from the Office of Emergency Management headquarters. (Citation: Mark Loveless April 2017) MITRE source; not an assessment.
Note on A4: Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to enable remote service abuse. A common goal for post-compromise exploitation of remote services is for initial access into and lateral movement throughout the ICS environment to enable access to targeted systems. (Citation: Enterprise ATT&CK) ICS asset owners and operators have been affected by ransomware (or disruptive malware masquerading as ransomware) migrating from enterprise IT to ICS environments: WannaCry, NotPetya, and BadRabbit. In each of these cases, self-propagating (wormable) malware initially infected IT networks, but through exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks, producing significant impacts. (Citation: Joe Slowik April 2019) MITRE source; not an assessment.
Note on B4: Adversaries may utilize command-line interfaces (CLIs) to interact with systems and execute commands. CLIs provide a means of interacting with computer systems and are a common feature across many types of platforms and devices within control systems environments. (Citation: Enterprise ATT&CK January 2018) Adversaries may also use CLIs to install and run new software, including malicious tools that may be installed over the course of an operation. CLIs are typically accessed locally, but can also be exposed via services, such as SSH, Telnet, and RDP. Commands that are executed in the CLI execute with the current permissions level of the process running the terminal emulator, unless the command specifies a change in permissions context. Many controllers have CLI interfaces for management purposes. MITRE source; not an assessment.
Note on C4: Adversaries may leverage credentials that are hardcoded in software or firmware to gain an unauthorized interactive user session to an asset. Examples credentials that may be hardcoded in an asset include: * Username/Passwords * Cryptographic keys/Certificates * API tokens Unlike Default Credentials, these credentials are built into the system in a way that they either cannot be changed by the asset owner, or may be infeasible to change because of the impact it would cause to the control system operation. These credentials may be reused across whole product lines or device models and are often not published or known to the owner and operators of the asset.(Citation: ICS-ALERT-13-164-01)(Citation: OT IceFall) Adversaries may utilize these hardcoded credentials to move throughout the control system environment or provide reliable access for their tools to interact with industrial assets. MITRE source; not an assessment.
Note on E4: Adversaries may attempt to remove indicators of their presence on a system in an effort to cover their tracks. In cases where an adversary may feel detection is imminent, they may try to overwrite, delete, or cover up changes they have made to the device. MITRE source; not an assessment.
Note on F4: Adversaries may attempt to get a listing of other systems by IP address, hostname, or other logical identifier on a network that may be used for subsequent Lateral Movement or Discovery techniques. Functionality could exist within adversary tools to enable this, but utilities available on the operating system or vendor software could also be used.(Citation: Enterprise ATT&CK January 2018) MITRE source; not an assessment.
Note on G4: Adversaries may leverage manufacturer or supplier set default credentials on control system devices. These default credentials may have administrative permissions and may be necessary for initial configuration of the device. It is general best practice to change the passwords for these accounts as soon as possible, but some manufacturers may have devices that have passwords or usernames that cannot be changed.(Citation: Keith Stouffer May 2015) Default credentials are normally documented in an instruction manual that is either packaged with the device, published online through official means, or published online through unofficial means. Adversaries may leverage default credentials that have not been properly modified or disabled. MITRE source; not an assessment.
Note on H4: Adversaries may target and collect data from information repositories. This can include sensitive data such as specifications, schematics, or diagrams of control system layouts, devices, and processes. Examples of information repositories include reference databases in the process environment, as well as databases in the corporate network that might contain information about the ICS.(Citation: Cybersecurity & Infrastructure Security Agency March 2018) Information collected from these systems may provide the adversary with a better understanding of the operational environment, vendors used, processes, or procedures of the ICS. In a campaign between 2011 and 2013 against ONG organizations, Chinese state-sponsored actors searched document repositories for specific information such as, system manuals, remote terminal unit (RTU) sites, personnel lists, documents that included the string SCAD*, user credentials, and remote dial-up access information. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) MITRE source; not an assessment.
Note on I4: Adversaries may establish command and control capabilities over commonly used application layer protocols such as HTTP(S), OPC, RDP, telnet, DNP3, and modbus. These protocols may be used to disguise adversary actions as benign network traffic. Standard protocols may be seen on their associated port or in some cases over a non-standard port. Adversaries may use these protocols to reach out of the network for command and control, or in some cases to other infected devices within the network. MITRE source; not an assessment.
Note on J4: Operational technology communications occur over serial COM, Ethernet, Wi-Fi, cellular (4G/5G), and satellite mediums. Adversaries may block communications to prevent reporting messages and command messages from reaching their intended target devices disrupting processes, operations, and causing cyber-physical impacts.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) Adversaries may block communications by either making modifications to software (System Firmware, Module Firmware, Hooking, and Rootkit) and services (Service Stop, Denial of Service) on systems and devices or by positioning themselves between systems and devices and intercepting and blocking the communications such as the case with an Adversary-in-the-Middle attack. MITRE source; not an assessment.
Note on K4: System firmware on modern assets is often designed with an update feature. Older device firmware may be factory installed and require special reprograming equipment. When available, the firmware update feature enables vendors to remotely patch bugs and perform upgrades. Device firmware updates are often delegated to the user and may be done using a software update package. It may also be possible to perform this task over the network. An adversary may exploit the firmware update feature on accessible devices to upload malicious or out-of-date firmware. Malicious modification of device firmware may provide an adversary with root access to a device, given firmware is one of the lowest programming abstraction layers.(Citation: Basnight, Zachry, et al.) MITRE source; not an assessment.
Note on L4: Adversaries may cause a denial of view in attempt to disrupt and prevent operator oversight on the status of an ICS environment. This may manifest itself as a temporary communication failure between a device and its control source, where the interface recovers and becomes available once the interference ceases. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) An adversary may attempt to deny operator visibility by preventing them from receiving status and reporting messages. Denying this view may temporarily block and prevent operators from noticing a change in state or anomalous behavior. The environment's data and processes may still be operational, but functioning in an unintended or adversarial manner. MITRE source; not an assessment.
Note on A5: Adversaries may leverage external remote services as a point of initial access into your network. These services allow users to connect to internal network resources from external locations. Examples are VPNs, Citrix, and other access mechanisms. Remote service gateways often manage connections and credential authentication for these services. (Citation: Daniel Oakley, Travis Smith, Tripwire) External remote services allow administration of a control system from outside the system. Often, vendors and internal engineering groups have access to external remote services to control system networks via the corporate network. In some cases, this access is enabled directly from the internet. While remote access enables ease of maintenance when a control system is in a remote area, compromise of remote access solutions is a liability. The adversary may use these services to gain access to and execute attacks against a control system network. Access to valid accounts is often a requirement. As they look for an entry point into the control system network, adversaries may begin searching for existing point-to-point VPN implementations at trusted third party networks or through remote support employee connections where split tunneling is enabled. (Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) MITRE source; not an assessment.
Note on B5: Adversaries may attempt to leverage Application Program Interfaces (APIs) used for communication between control software and the hardware. Specific functionality is often coded into APIs which can be called by software to engage specific functions on a device or other software. MITRE source; not an assessment.
Note on C5: Firmware is low-level software embedded in hardware that enables systems and devices to function properly and is commonly found in ICS environments. Adversaries may modify firmware on a system or device by installing malicious or vulnerable versions that enable them to achieve objectives such as Persistence, Impair Process Control, and Inhibit Response Function. Adversaries may modify system and device firmware by using the built-in firmware update functionality which may support local or remote installation. The malicious or vulnerable firmware may be delivered via Replication Through Removable Media, Supply Chain Compromise, or Remote Services. Once installed, the malicious or vulnerable firmware could be used to provide Rootkit and Hooking functionality, Exploitation for Privilege Escalation, or Denial of Service.(Citation: Basnight, Zachry, et al.) MITRE source; not an assessment.
Note on E5: Adversaries may use masquerading to disguise a malicious application or executable as another file, to avoid operator and engineer suspicion. Possible disguises of these masquerading files can include commonly found programs, expected vendor executables and configuration files, and other commonplace application and naming conventions. By impersonating expected and vendor-relevant files and applications, operators and engineers may not notice the presence of the underlying malicious content and possibly end up running those masquerading as legitimate functions. Applications and other files commonly found on Windows systems or in engineering workstations have been impersonated before. This can be as simple as renaming a file to effectively disguise it in the ICS environment. MITRE source; not an assessment.
Note on F5: Adversaries may perform a port scan on a system, device, or network to identify live hosts, enumerate open ports and running services, identify operating systems, and map out the network.(Citation: NIST SP 800-82r3) The results of a port scan may inform adversary Discovery, Lateral Movement, and vulnerability exploitation decisions (Exploitation for Evasion, Exploitation for Privilege Escalation, Exploitation of Remote Services). Some common tools for executing a port scan include nmap, netcat, and the Advanced Port Scanner. MITRE source; not an assessment.
Note on G5: Adversaries may leverage credentials that are hardcoded in software or firmware to gain an unauthorized interactive user session to an asset. Examples credentials that may be hardcoded in an asset include: * Username/Passwords * Cryptographic keys/Certificates * API tokens Unlike Default Credentials, these credentials are built into the system in a way that they either cannot be changed by the asset owner, or may be infeasible to change because of the impact it would cause to the control system operation. These credentials may be reused across whole product lines or device models and are often not published or known to the owner and operators of the asset.(Citation: ICS-ALERT-13-164-01)(Citation: OT IceFall) Adversaries may utilize these hardcoded credentials to move throughout the control system environment or provide reliable access for their tools to interact with industrial assets. MITRE source; not an assessment.
Note on H5: Adversaries may target and collect data from local system sources, such as file systems, configuration files, or local databases. This can include sensitive data such as specifications, schematics, or diagrams of control system layouts, devices, and processes. Adversaries may do this using Command-Line Interface or Scripting techniques to interact with the file system to gather information. Adversaries may also use Automated Collection on the local system. MITRE source; not an assessment.
Note on J5: Adversaries may block access to serial COM to prevent instructions or configurations from reaching target devices. Serial Communication ports (COM) allow communication with control system devices. Devices can receive command and configuration messages over such serial COM. Devices also use serial COM to send command and reporting messages. Blocking device serial COM may also block command messages and block reporting messages. A serial to Ethernet converter is often connected to a serial COM to facilitate communication between serial and Ethernet devices. One approach to blocking a serial COM would be to create and hold open a TCP session with the Ethernet side of the converter. A serial to Ethernet converter may have a few ports open to facilitate multiple communications. For example, if there are three serial COM available -- 1, 2 and 3 --, the converter might be listening on the corresponding ports 20001, 20002, and 20003. If a TCP/IP connection is opened with one of these ports and held open, then the port will be unavailable for use by another party. One way the adversary could achieve this would be to initiate a TCP session with the serial to Ethernet converter at 10.0.0.1 via Telnet on serial port 1 with the following command: telnet 10.0.0.1 20001. MITRE source; not an assessment.
Note on K5: Adversaries may install malicious or vulnerable firmware onto modular hardware devices. Control system devices often contain modular hardware devices. These devices may have their own set of firmware that is separate from the firmware of the main control system equipment. This technique is similar to System Firmware, but is conducted on other system components that may not have the same capabilities or level of integrity checking. Although it results in a device re-image, malicious device firmware may provide persistent access to remaining devices.(Citation: Daniel Peck, Dale Peterson January 2009) An easy point of access for an adversary is the Ethernet card, which may have its own CPU, RAM, and operating system. The adversary may attack and likely exploit the computer on an Ethernet card. Exploitation of the Ethernet card computer may enable the adversary to accomplish additional attacks, such as the following:(Citation: Daniel Peck, Dale Peterson January 2009) * Delayed Attack - The adversary may stage an attack in advance and choose when to launch it, such as at a particularly damaging time. * Brick the Ethernet Card - Malicious firmware may be programmed to result in an Ethernet card failure, requiring a factory return. * Random Attack or Failure - The adversary may load malicious firmware onto multiple field devices. Execution of an attack and the time it occurs is generated by a pseudo-random number generator. * A Field Device Worm - The adversary may choose to identify all field devices of the same model, with the end goal of performing a device-wide compromise. * Attack Other Cards on the Field Device - Although it is not the most important module in a field device, the Ethernet card is most accessible to the adversary and malware. Compromise of the Ethernet card may provide a more direct route to compromising other modules, such as the CPU module. MITRE source; not an assessment.
Note on L5: Adversaries may attempt to disrupt essential components or systems to prevent owner and operator from delivering products or services. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) Adversaries may leverage malware to delete or encrypt critical data on HMIs, workstations, or databases. In the 2021 Colonial Pipeline ransomware incident, pipeline operations were temporally halted on May 7th and were not fully restarted until May 12th. (Citation: Colonial Pipeline Company May 2021) MITRE source; not an assessment.
Note on A6: Adversaries may gain access into industrial environments through systems exposed directly to the internet for remote access rather than through External Remote Services. Internet Accessible Devices are exposed to the internet unintentionally or intentionally without adequate protections. This may allow for adversaries to move directly into the control system network. Access onto these devices is accomplished without the use of exploits, these would be represented within the Exploit Public-Facing Application technique. Adversaries may leverage built in functions for remote access which may not be protected or utilize minimal legacy protections that may be targeted. (Citation: NCCIC January 2014) These services may be discoverable through the use of online scanning tools. In the case of the Bowman dam incident, adversaries leveraged access to the dam control network through a cellular modem. Access to the device was protected by password authentication, although the application was vulnerable to brute forcing. (Citation: NCCIC January 2014) (Citation: Danny Yadron December 2015) (Citation: Mark Thompson March 2016) In Trend Micros manufacturing deception operations adversaries were detected leveraging direct internet access to an ICS environment through the exposure of operational protocols such as Siemens S7, Omron FINS, and EtherNet/IP, in addition to misconfigured VNC access. (Citation: Stephen Hilt, Federico Maggi, Charles Perine, Lord Remorin, Martin Rsler, and Rainer Vosseler) MITRE source; not an assessment.
Note on B6: Adversaries may attempt to gain access to a machine via a Graphical User Interface (GUI) to enhance execution capabilities. Access to a GUI allows a user to interact with a computer in a more visual manner than a CLI. A GUI allows users to move a cursor and click on interface objects, with a mouse and keyboard as the main input devices, as opposed to just using the keyboard. If physical access is not an option, then access might be possible via protocols such as VNC on Linux-based and Unix-based operating systems, and RDP on Windows operating systems. An adversary can use this access to execute programs and applications on the target machine. MITRE source; not an assessment.
Note on C6: System firmware on modern assets is often designed with an update feature. Older device firmware may be factory installed and require special reprograming equipment. When available, the firmware update feature enables vendors to remotely patch bugs and perform upgrades. Device firmware updates are often delegated to the user and may be done using a software update package. It may also be possible to perform this task over the network. An adversary may exploit the firmware update feature on accessible devices to upload malicious or out-of-date firmware. Malicious modification of device firmware may provide an adversary with root access to a device, given firmware is one of the lowest programming abstraction layers.(Citation: Basnight, Zachry, et al.) MITRE source; not an assessment.
Note on E6: Adversaries may deploy rootkits to hide the presence of programs, files, network connections, services, drivers, and other system components. Rootkits are programs that hide the existence of malware by intercepting and modifying operating-system API calls that supply system information. Rootkits or rootkit-enabling functionality may reside at the user or kernel level in the operating system, or lower. (Citation: Enterprise ATT&CK January 2018) Firmware rootkits that affect the operating system yield nearly full control of the system. While firmware rootkits are normally developed for the main processing board, they can also be developed for the I/O that is attached to an asset. Compromise of this firmware allows the modification of all of the process variables and functions the module engages in. This may result in commands being disregarded and false information being fed to the main device. By tampering with device processes, an adversary may inhibit its expected response functions and possibly enable Impact. MITRE source; not an assessment.
Note on F6: Adversaries may perform broadcast discovery requests to enumerate systems and devices on a network. Broadcast discovery works by one system or device sending messages to all systems and devices on a network (or subnet) and then waiting for a response. If a response is received that means the system or device that responded is live and can communicate over that protocol. Adversaries may leverage different protocols supported on the network for sending broadcast messages. Some common OT protocols that have broadcast discovery mechanisms are Building Automation and Control Network (BACNet) Who-Is requests, Common Industrial Protocol (CIP) List Identity User Datagram Protocol (UDP) broadcast requests, and Siemens S7 broadcast identification requests.(Citation: Broadcasting BACnet)(Citation: Cisco Active Discovery) MITRE source; not an assessment.
Note on G6: Adversaries may transfer tools or other files from one system to another to stage adversary tools or other files over the course of an operation. (Citation: Enterprise ATT&CK) Copying of files may also be performed laterally between internal victim systems to support Lateral Movement with remote Execution using inherent file sharing protocols such as file sharing over SMB to connected network shares. (Citation: Enterprise ATT&CK) In control systems environments, malware may use SMB and other file sharing protocols to move laterally through industrial networks. MITRE source; not an assessment.
Note on H6: Adversaries may gather information about a PLCs or controllers current operating mode. Operating modes dictate what change or maintenance functions can be manipulated and are often controlled by a key switch on the PLC (e.g., run, prog [program], and remote). Knowledge of these states may be valuable to an adversary to determine if they are able to reprogram the PLC. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: * Program - This mode must be enabled before changes can be made to a devices program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLCs logic Is halted, and all outputs may be forced off. (Citation: N.A. October 2017) * Run - Execution of the devices program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the programs logic.Program Upload and Program Download are disabled while in this mode. (Citation: Omron) (Citation: Machine Information Systems 2007) (Citation: N.A. October 2017) (Citation: PLCgurus 2021) * Remote - Allows for remote changes to a PLCs operation mode. (Citation: PLCgurus 2021) * Stop - The PLC and program is stopped, while in this mode, outputs are forced off. (Citation: Machine Information Systems 2007) * Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. (Citation: Machine Information Systems 2007) * Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. (Citation: Omron) MITRE source; not an assessment.
Note on J6: Adversaries may block access to Ethernet communications to prevent instructions or configurations messages from reaching target systems and devices. Ethernet connections allow for communications between IT and OT systems and devices. Blocking Ethernet communications may also block command and reporting messages.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) An adversary may block Ethernet communications by disabling network interfaces, Service Stop, or conducting an Adversary-in-the-Middle attack and dropping the network traffic. MITRE source; not an assessment.
Note on K6: Adversaries may modify parameters used to instruct industrial control system devices. These devices operate via programs that dictate how and when to perform actions based on such parameters. Such parameters can determine the extent to which an action is performed and may specify additional options. For example, a program on a control system device dictating motor processes may take a parameter defining the total number of seconds to run that motor. An adversary can potentially modify these parameters to produce an outcome outside of what was intended by the operators. By modifying system and process critical parameters, the adversary may cause Impact to equipment and/or control processes. Modified parameters may be turned into dangerous, out-of-bounds, or unexpected values from typical operations. For example, specifying that a process run for more or less time than it should, or dictating an unusually high, low, or invalid value as a parameter. MITRE source; not an assessment.
Note on L6: Adversaries may seek to achieve a sustained loss of control or a runaway condition in which operators cannot issue any commands even if the malicious interference has subsided. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill in its 2014 IT Security Report.(Citation: BSI State of IT Security 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact resulted in damage and unsafe conditions from the uncontrolled shutdown of a blast furnace. MITRE source; not an assessment.
Note on A7: Adversaries may leverage remote services to move between assets and network segments. These services are often used to allow operators to interact with systems remotely within the network, some examples are RDP, SMB, SSH, and other similar mechanisms. (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) (Citation: Dragos December 2017) (Citation: Joe Slowik April 2019) Remote services could be used to support remote access, data transmission, authentication, name resolution, and other remote functions. Further, remote services may be necessary to allow operators and administrators to configure systems within the network from their engineering or management workstations. An adversary may use this technique to access devices which may be dual-homed (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) to multiple network segments, and can be used for Program Download or to execute attacks on control devices directly through Valid Accounts. Specific remote services (RDP & VNC) may be a precursor to enable Graphical User Interface execution on devices such as HMIs or engineering workstation software. Based on incident data, CISA and FBI assessed that Chinese state-sponsored actors also compromised various authorized remote access channels, including systems designed to transfer data and/or allow access between corporate and ICS networks. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) MITRE source; not an assessment.
Note on B7: Adversaries may hook into application programming interface (API) functions used by processes to redirect calls for execution and privilege escalation means. Windows processes often leverage these API functions to perform tasks that require reusable system resources. Windows API functions are typically stored in dynamic-link libraries (DLLs) as exported functions. (Citation: Enterprise ATT&CK) One type of hooking seen in ICS involves redirecting calls to these functions via import address table (IAT) hooking. IAT hooking uses modifications to a process IAT, where pointers to imported API functions are stored. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) MITRE source; not an assessment.
Note on C7: Adversaries may install malicious or vulnerable firmware onto modular hardware devices. Control system devices often contain modular hardware devices. These devices may have their own set of firmware that is separate from the firmware of the main control system equipment. This technique is similar to System Firmware, but is conducted on other system components that may not have the same capabilities or level of integrity checking. Although it results in a device re-image, malicious device firmware may provide persistent access to remaining devices.(Citation: Daniel Peck, Dale Peterson January 2009) An easy point of access for an adversary is the Ethernet card, which may have its own CPU, RAM, and operating system. The adversary may attack and likely exploit the computer on an Ethernet card. Exploitation of the Ethernet card computer may enable the adversary to accomplish additional attacks, such as the following:(Citation: Daniel Peck, Dale Peterson January 2009) * Delayed Attack - The adversary may stage an attack in advance and choose when to launch it, such as at a particularly damaging time. * Brick the Ethernet Card - Malicious firmware may be programmed to result in an Ethernet card failure, requiring a factory return. * Random Attack or Failure - The adversary may load malicious firmware onto multiple field devices. Execution of an attack and the time it occurs is generated by a pseudo-random number generator. * A Field Device Worm - The adversary may choose to identify all field devices of the same model, with the end goal of performing a device-wide compromise. * Attack Other Cards on the Field Device - Although it is not the most important module in a field device, the Ethernet card is most accessible to the adversary and malware. Compromise of the Ethernet card may provide a more direct route to compromising other modules, such as the CPU module. MITRE source; not an assessment.
Note on E7: Adversaries may bypass process and/or signature-based defenses by proxying execution of malicious content with signed, or otherwise trusted, binaries. Binaries used in this technique are often Microsoft-signed files, indicating that they have been either downloaded from Microsoft or are already native in the operating system. (Citation: LOLBAS Project) Binaries signed with trusted digital certificates can typically execute on Windows systems protected by digital signature validation. Several Microsoft signed binaries that are default on Windows installations can be used to proxy execution of other files or commands. Similarly, on Linux systems adversaries may abuse trusted binaries such as split to proxy execution of malicious commands. (Citation: split man page)(Citation: GTFO split) Adversaries may abuse application binaries installed on a system for proxy execution of malicious code or domain-specific commands. These commands could be used to target local resources on the device or networked devices within the environment through defined APIs (Execution through API) or application-specific programming languages (e.g., MicroSCADA SCIL). Application binaries may be signed by the developer or generally trusted by the operators, analysts, and monitoring tools accustomed to the environment. These applications may be developed and/or directly provided by the device vendor to enable configuration, management, and operation of their devices without many alternatives. Adversaries may seek to target these trusted application binaries to execute or send commands without the development of custom malware. For example, adversaries may target a SCADA server binary which has the existing ability to send commands to substation devices, such as through IEC 104 command messages. Proxy execution may still require the development of custom tools to hook into the application binary’s execution. MITRE source; not an assessment.
Note on F7: Adversaries may perform multicast discovery requests which is when one system or device sends messages to all systems and devices in a pre-defined group on a network (or subnet) and then waits for a response. If a response is received that means the system or device that responded is live and can communicate over that protocol. Multicast discovery tends to be stealthier than broadcast discovery because every system or device on the network (or subnet) is not being messaged. One common OT protocol that has a multicast discovery mechanism is the Process Field Network (PROFINET) Discovery and Configuration Protocol (DCP) with its Identify All requests.(Citation: Cisco Active Discovery) MITRE source; not an assessment.
Note on G7: Adversaries may perform a program download to transfer a user program to a controller. Variations of program download, such as online edit and program append, allow a controller to continue running during the transfer and reconfiguration process without interruption to process control. However, before starting a full program download (i.e., download all) a controller may need to go into a stop state. This can have negative consequences on the physical process, especially if the controller is not able to fulfill a time-sensitive action. Adversaries may choose to avoid a download all in favor of an online edit or program append to avoid disrupting the physical process. An adversary may need to use the technique Detect Operating Mode or Change Operating Mode to make sure the controller is in the proper mode to accept a program download. The granularity of control to transfer a user program in whole or parts is dictated by the management protocol (e.g., S7CommPlus, TriStation) and underlying controller API. Thus, program download is a high-level term for the suite of vendor-specific API calls used to configure a controllers user program memory space. Modify Controller Tasking and Modify Program represent the configuration changes that are transferred to a controller via a program download. MITRE source; not an assessment.
Note on H7: Adversaries may seek to capture process values related to the inputs and outputs of a PLC. During the scan cycle, a PLC reads the status of all inputs and stores them in an image table. (Citation: Nanjundaiah, Vaidyanath) The image table is the PLCs internal storage location where values of inputs/outputs for one scan are stored while it executes the user program. After the PLC has solved the entire logic program, it updates the output image table. The contents of this output image table are written to the corresponding output points in I/O Modules. The Input and Output Image tables described above make up the I/O Image on a PLC. This image is used by the user program instead of directly interacting with physical I/O. (Citation: Spenneberg, Ralf 2016) Adversaries may collect the I/O Image state of a PLC by utilizing a devices Native API to access the memory regions directly. The collection of the PLCs I/O state could be used to replace values or inform future stages of an attack. MITRE source; not an assessment.
Note on J7: Adversaries may block access to Wi-Fi communications to prevent messages from reaching target systems and devices. Wi-Fi connections allow for communications between IT and OT systems and devices. Blocking Wi-Fi communications may also block command and reporting messages.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) An adversary may block Wi-Fi communications by disabling network interfaces, Service Stop, conducting an Adversary-in-the-Middle attack and dropping the network traffic, or by jamming the Wi-Fi signal. MITRE source; not an assessment.
Note on K7: Adversaries may send unauthorized messages to ICS systems and devices to evade defenses or manipulate processes. Unauthorized messages can be categorized as either reporting messages that contain telemetry data about the current state of systems, devices, and processes or as command messages which instruct systems and devices on how to operate. By injecting unauthorized messages, adversaries can make it appear as if everything is working correctly when it isn’t, trigger alarms to misdirect personnel or impact processes, and manipulate controls to disrupt processes.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) Adversaries may send unauthorized messages in an ICS environment using software found within the environment (living-off-the-land, vendor-specific interfaces, etc.), custom tooling leveraging OT protocols and libraries, or by positioning themselves between systems and devices and injecting messages into the communications such as the case with an Adversary-in-the-Middle attack. MITRE source; not an assessment.
Note on L7: Adversaries may cause loss of productivity and revenue through disruption and even damage to the availability and integrity of control system operations, devices, and related processes. This technique may manifest as a direct effect of an ICS-targeting attack or tangentially, due to an IT-targeting attack against non-segregated environments. In cases where these operations or services are brought to a halt, the loss of productivity may eventually present an impact for the end-users or consumers of products and services. The disrupted supply-chain may result in supply shortages and increased prices, among other consequences. A ransomware attack on an Australian beverage company resulted in the shutdown of some manufacturing sites, including precautionary halts to protect key systems. (Citation: Paganini, Pierluigi June 2020) The company announced the potential for temporary shortages of their products following the attack. (Citation: Paganini, Pierluigi June 2020) (Citation: Lion Corporation June 2020) In the 2021 Colonial Pipeline ransomware incident, the pipeline was unable to transport approximately 2.5 million barrels of fuel per day to the East Coast. (Citation: Colonial Pipeline Company May 2021) MITRE source; not an assessment.
Note on A8: Adversaries may move onto systems, such as those separated from the enterprise network, by copying malware to removable media which is inserted into the control systems environment. The adversary may rely on unknowing trusted third parties, such as suppliers or contractors with access privileges, to introduce the removable media. This technique enables initial access to target devices that never connect to untrusted networks, but are physically accessible. Operators of the German nuclear power plant, Gundremmingen, discovered malware on a facility computer not connected to the internet. (Citation: Kernkraftwerk Gundremmingen April 2016) (Citation: Trend Micro April 2016) The malware included Conficker and W32.Ramnit, which were also found on eighteen removable disk drives in the facility. (Citation: Christoph Steitz, Eric Auchard April 2016) (Citation: Catalin Cimpanu April 2016) (Citation: Peter Dockrill April 2016) (Citation: Lee Mathews April 2016) (Citation: Sean Gallagher April 2016) (Citation: Dark Reading Staff April 2016) The plant has since checked for infection and cleaned up more than 1,000 computers. (Citation: BBC April 2016) An ESET researcher commented that internet disconnection does not guarantee system safety from infection or payload execution. (Citation: ESET April 2016) MITRE source; not an assessment.
Note on B8: Adversaries may modify the tasking of a controller to allow for the execution of their own programs. This can allow an adversary to manipulate the execution flow and behavior of a controller. According to 61131-3, the association of a Task with a Program Organization Unit (POU) defines a task association. (Citation: IEC February 2013) An adversary may modify these associations or create new ones to manipulate the execution flow of a controller. Modification of controller tasking can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Tasks have properties, such as interval, frequency and priority to meet the requirements of program execution. Some controller vendors implement tasks with implicit, pre-defined properties whereas others allow for these properties to be formulated explicitly. An adversary may associate their program with tasks that have a higher priority or execute associated programs more frequently. For instance, to ensure cyclic execution of their program on a Siemens controller, an adversary may add their program to the task, Organization Block 1 (OB1). MITRE source; not an assessment.
Note on C8: Adversaries may modify or add a program on a controller to affect how it interacts with the physical process, peripheral devices and other hosts on the network. Modification to controller programs can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Program modification encompasses the addition and modification of instructions and logic contained in Program Organization Units (POU) (Citation: IEC February 2013) and similar programming elements found on controllers. This can include, for example, adding new functions to a controller, modifying the logic in existing functions and making new calls from one function to another. Some programs may allow an adversary to interact directly with the native API of the controller to take advantage of obscure features or vulnerabilities. MITRE source; not an assessment.
Note on E8: Adversaries may send unauthorized messages to ICS systems and devices to evade defenses or manipulate processes. Unauthorized messages can be categorized as either reporting messages that contain telemetry data about the current state of systems, devices, and processes or as command messages which instruct systems and devices on how to operate. By injecting unauthorized messages, adversaries can make it appear as if everything is working correctly when it isn’t, trigger alarms to misdirect personnel or impact processes, and manipulate controls to disrupt processes.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) Adversaries may send unauthorized messages in an ICS environment using software found within the environment (living-off-the-land, vendor-specific interfaces, etc.), custom tooling leveraging OT protocols and libraries, or by positioning themselves between systems and devices and injecting messages into the communications such as the case with an Adversary-in-the-Middle attack. MITRE source; not an assessment.
Note on F8: An adversary may attempt to get detailed information about remote systems and their peripherals, such as make/model, role, and configuration. Adversaries may use information from Remote System Information Discovery to aid in targeting and shaping follow-on behaviors. For example, the system's operational role and model information can dictate whether it is a relevant target for the adversary's operational objectives. In addition, the system's configuration may be used to scope subsequent technique usage. Requests for system information are typically implemented using automation and management protocols and are often automatically requested by vendor software during normal operation. This information may be used to tailor management actions, such as program download and system or module firmware. An adversary may leverage this same information by issuing calls directly to the system's API. MITRE source; not an assessment.
Note on G8: Adversaries may execute a full program download to a PLC to overwrite the entire PLC program and configuration to deploy a new project or make major changes. This typically requires stopping the PLC and adversely impacting control processes. The ability to perform a full program download to the PLC typically relies on access to a workstation with the vendor-specific PLC programming software installed. MITRE source; not an assessment.
Note on H8: Adversaries may gather information about the physical process state. This information may be used to gain more information about the process itself or used as a trigger for malicious actions. The sources of process state information may vary such as, OPC tags, historian data, specific PLC block information, or network traffic. MITRE source; not an assessment.
Note on J8: Adversaries may block messages between systems and devices in an OT/ICS environment to disrupt processes. Messages typically fall into two categories: (1) reporting messages that contain telemetry data about the current state of systems, devices, and processes and (2) command messages that contain instructions to control systems, devices, and processes. Both types of messages are critical for the proper functioning of industrial control processes and failure of the messages to reach their intended destinations could inhibit response functions or create an unsafe condition that could have physical impacts.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011)(Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) Adversaries may block communications by either making modifications to software (System Firmware, Module Firmware, Hooking, and Rootkit) and services (Service Stop, Denial of Service) on systems and devices or by positioning themselves between systems and devices and intercepting and blocking the communications such as the case with an Adversary-in-the-Middle attack. MITRE source; not an assessment.
Note on K8: Adversaries may send unauthorized command messages to instruct control system assets to perform actions outside of their intended functionality, or without the logical preconditions to trigger their expected function. Command messages are used in ICS networks to give direct instructions to control systems devices. If an adversary can send an unauthorized command message to a control system, then it can instruct the control systems device to perform an action outside the normal bounds of the device's actions. An adversary could potentially instruct a control systems device to perform an action that will cause an Impact.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) In the Dallas Siren incident, adversaries were able to send command messages to activate tornado alarm systems across the city without an impending tornado or other disaster.(Citation: Zack Whittaker April 2017)(Citation: Benjamin Freed March 2019) MITRE source; not an assessment.
Note on L8: Adversaries may compromise protective system functions designed to prevent the effects of faults and abnormal conditions. This can result in equipment damage, prolonged process disruptions and hazards to personnel. Many faults and abnormal conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable protective system functions as a prerequisite to subsequent attack execution or to allow for future faults and abnormal conditions to go unchecked. Detection of a Loss of Protection by operators can result in the shutdown of a process due to strict policies regarding protection systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. MITRE source; not an assessment.
Note on A9: Adversaries may setup a rogue master to leverage control server functions to communicate with outstations. A rogue master can be used to send legitimate control messages to other control system devices, affecting processes in unintended ways. It may also be used to disrupt network communications by capturing and receiving the network traffic meant for the actual master. Impersonating a master may also allow an adversary to avoid detection. In the case of the 2017 Dallas Siren incident, adversaries used a rogue master to send command messages to the 156 distributed sirens across the city, either through a single rogue transmitter with a strong signal, or using many distributed repeaters. (Citation: Bastille April 2017) (Citation: Zack Whittaker April 2017) MITRE source; not an assessment.
Note on B9: Adversaries may directly interact with the native OS application programming interface (API) to access system functions. Native APIs provide a controlled means of calling low-level OS services within the kernel, such as those involving hardware/devices, memory, and processes. (Citation: The MITRE Corporation May 2017) These native APIs are leveraged by the OS during system boot (when other system components are not yet initialized) as well as carrying out tasks and requests during routine operations. Functionality provided by native APIs are often also exposed to user-mode applications via interfaces and libraries. For example, functions such as memcpy and direct operations on memory registers can be used to modify user and system memory space. MITRE source; not an assessment.
Note on C9: Adversaries may attempt to infect project files with malicious code. These project files may consist of objects, program organization units, variables such as tags, documentation, and other configurations needed for PLC programs to function.(Citation: Beckhoff) Using built in functions of the engineering software, adversaries may be able to download an infected program to a PLC in the operating environment enabling further Execution and Persistence techniques.(Citation: PLCdev) Adversaries may export their own code into project files with conditions to execute at specific intervals.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) Malicious programs allow adversaries control of all aspects of the process enabled by the PLC. Once the project file is downloaded to a PLC the workstation device may be disconnected with the infected project file still executing.(Citation: PLCdev) MITRE source; not an assessment.
Note on E9: Adversaries may send unauthorized command messages to instruct control system assets to perform actions outside of their intended functionality, or without the logical preconditions to trigger their expected function. Command messages are used in ICS networks to give direct instructions to control systems devices. If an adversary can send an unauthorized command message to a control system, then it can instruct the control systems device to perform an action outside the normal bounds of the device's actions. An adversary could potentially instruct a control systems device to perform an action that will cause an Impact.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) In the Dallas Siren incident, adversaries were able to send command messages to activate tornado alarm systems across the city without an impending tornado or other disaster.(Citation: Zack Whittaker April 2017)(Citation: Benjamin Freed March 2019) MITRE source; not an assessment.
Note on F9: Adversaries may seek to capture radio frequency (RF) communication used for remote control and reporting in distributed environments. RF communication frequencies vary between 3 kHz to 300 GHz, although are commonly between 300 MHz to 6 GHz. (Citation: Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K. April 2018) The wavelength and frequency of the signal affect how the signal propagates through open air, obstacles (e.g. walls and trees) and the type of radio required to capture them. These characteristics are often standardized in the protocol and hardware and may have an effect on how the signal is captured. Some examples of wireless protocols that may be found in cyber-physical environments are: WirelessHART, Zigbee, WIA-FA, and 700 MHz Public Safety Spectrum. Adversaries may capture RF communications by using specialized hardware, such as software defined radio (SDR), handheld radio, or a computer with radio demodulator tuned to the communication frequency. (Citation: Bastille April 2017) Information transmitted over a wireless medium may be captured in-transit whether the sniffing device is the intended destination or not. This technique may be particularly useful to an adversary when the communications are not encrypted. (Citation: Gallagher, S. April 2017) In the 2017 Dallas Siren incident, it is suspected that adversaries likely captured wireless command message broadcasts on a 700 MHz frequency during a regular test of the system. These messages were later replayed to trigger the alarm systems. (Citation: Gallagher, S. April 2017) MITRE source; not an assessment.
Note on G9: Adversaries may execute an online edit of a PLC to update parts of an existing program. It does not require stopping the PLC which allows it to continue running during transfer and reconfiguration without interruption to process control. Adversaries may leverage this approach to minimize downtime and evade detection. The ability to perform an online edit to the PLC typically relies on access to a workstation with the vendor-specific PLC programming software installed. MITRE source; not an assessment.
Note on H9: Adversaries may collect point and tag values to gain a more comprehensive understanding of the process environment. Points may be values such as inputs, memory locations, outputs or other process specific variables. (Citation: Dennis L. Sloatman September 2016) Tags are the identifiers given to points for operator convenience. Collecting such tags provides valuable context to environmental points and enables an adversary to map inputs, outputs, and other values to their control processes. Understanding the points being collected may inform an adversary on which processes and values to keep track of over the course of an operation. MITRE source; not an assessment.
Note on J9: Adversaries may block a command message from reaching its intended target to prevent command execution. In OT networks, command messages are sent to provide instructions to control system devices. A blocked command message can inhibit response functions from correcting a disruption or unsafe condition.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011)(Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) MITRE source; not an assessment.
Note on K9: Adversaries may spoof reporting messages in control system environments for evasion and to impair process control. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. Reporting messages are important for monitoring the normal operation of a system or identifying important events such as deviations from expected values. If an adversary has the ability to Spoof Reporting Messages, they can impact the control system in many ways. The adversary can Spoof Reporting Messages that state that the process is operating normally, as a form of evasion. The adversary could also Spoof Reporting Messages to make the defenders and operators think that other errors are occurring in order to distract them from the actual source of a problem.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) MITRE source; not an assessment.
Note on L9: Adversaries may compromise safety system functions designed to maintain safe operation of a process when unacceptable or dangerous conditions occur. Safety systems are often composed of the same elements as control systems but have the sole purpose of ensuring the process fails in a predetermined safe manner. Many unsafe conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable safety system functions as a prerequisite to subsequent attack execution or to allow for future unsafe conditionals to go unchecked. Detection of a Loss of Safety by operators can result in the shutdown of a process due to strict policies regarding safety systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. MITRE source; not an assessment.
Note on A10: Adversaries may use a spearphishing attachment, a variant of spearphishing, as a form of a social engineering attack against specific targets. Spearphishing attachments are different from other forms of spearphishing in that they employ malware attached to an email. All forms of spearphishing are electronically delivered and target a specific individual, company, or industry. In this scenario, adversaries attach a file to the spearphishing email and usually rely upon User Execution to gain execution and access. (Citation: Enterprise ATT&CK October 2019) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012, targeted ONG organizations and their employees. The emails were constructed with a high level of sophistication to convince employees to open the malicious file attachments. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) MITRE source; not an assessment.
Note on B10: Adversaries may use scripting languages to execute arbitrary code in the form of a pre-written script or in the form of user-supplied code to an interpreter. Scripting languages are programming languages that differ from compiled languages, in that scripting languages use an interpreter, instead of a compiler. These interpreters read and compile part of the source code just before it is executed, as opposed to compilers, which compile each and every line of code to an executable file. Scripting allows software developers to run their code on any system where the interpreter exists. This way, they can distribute one package, instead of precompiling executables for many different systems. Scripting languages, such as Python, have their interpreters shipped as a default with many Linux distributions. In addition to being a useful tool for developers and administrators, scripting language interpreters may be abused by the adversary to execute code in the target environment. Due to the nature of scripting languages, this allows for weaponized code to be deployed to a target easily, and leaves open the possibility of on-the-fly scripting to perform a task. MITRE source; not an assessment.
Note on C10: Adversaries may infect Siemens PLC project files (i.e., Step 7, WinCC, etc.) to achieve Execution, Persistence, and Lateral Movement objectives. Adversaries may modify an existing project file or bring their own project files into the environment.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) The ability for an adversary to deploy an infected project file relies on access to a workstation with Siemens PLC programming software installed on it from which a program download can be performed. MITRE source; not an assessment.
Note on E10: Adversaries may spoof reporting messages in control system environments for evasion and to impair process control. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. Reporting messages are important for monitoring the normal operation of a system or identifying important events such as deviations from expected values. If an adversary has the ability to Spoof Reporting Messages, they can impact the control system in many ways. The adversary can Spoof Reporting Messages that state that the process is operating normally, as a form of evasion. The adversary could also Spoof Reporting Messages to make the defenders and operators think that other errors are occurring in order to distract them from the actual source of a problem.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) MITRE source; not an assessment.
Note on G10: Adversaries may execute a program append to a PLC to update parts of an existing program. It may or may not require stopping the PLC which may allow it to continue running during transfer and reconfiguration without interruption to process control. Adversaries may leverage this approach to minimize downtime and evade detection. The ability to perform a program append to the PLC typically relies on access to a workstation with the vendor-specific PLC programming software installed. MITRE source; not an assessment.
Note on H10: Adversaries may attempt to upload a program from a PLC to gather information about an industrial process. Uploading a program may allow them to acquire and study the underlying logic. Methods of program upload include vendor software, which enables the user to upload and read a program running on a PLC. This software can be used to upload the target program to a workstation, jump box, or an interfacing device. MITRE source; not an assessment.
Note on J10: Adversaries may block or prevent a reporting message from reaching its intended target. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. By blocking these reporting messages, an adversary can potentially hide their actions from an operator. Blocking reporting messages in control systems that manage physical processes may contribute to system impact, causing inhibition of a response function. A control system may not be able to respond in a proper or timely manner to an event, such as a dangerous fault, if its corresponding reporting message is blocked.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011)(Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) MITRE source; not an assessment.
Note on L10: Adversaries may cause a sustained or permanent loss of view where the ICS equipment will require local, hands-on operator intervention; for instance, a restart or manual operation. By causing a sustained reporting or visibility loss, the adversary can effectively hide the present state of operations. This loss of view can occur without affecting the physical processes themselves. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) MITRE source; not an assessment.
Note on A11: Adversaries may perform supply chain compromise to gain control systems environment access by means of infected products, software, and workflows. Supply chain compromise is the manipulation of products, such as devices or software, or their delivery mechanisms before receipt by the end consumer. Adversary compromise of these products and mechanisms is done for the goal of data or system compromise, once infected products are introduced to the target environment. Supply chain compromise can occur at all stages of the supply chain, from manipulation of development tools and environments to manipulation of developed products and tools distribution mechanisms. This may involve the compromise and replacement of legitimate software and patches, such as on third party or vendor websites. Targeting of supply chain compromise can be done in attempts to infiltrate the environments of a specific audience. In control systems environments with assets in both the IT and OT networks, it is possible a supply chain compromise affecting the IT environment could enable further access to the OT environment. Counterfeit devices may be introduced to the global supply chain posing safety and cyber risks to asset owners and operators. These devices may not meet the safety, engineering and manufacturing requirements of regulatory bodies but may feature tagging indicating conformance with industry standards. Due to the lack of adherence to standards and overall lesser quality, the counterfeit products may pose a serious safety and operational risk. (Citation: Control Global May 2019) Yokogawa identified instances in which their customers received counterfeit differential pressure transmitters using the Yokogawa logo. The counterfeit transmitters were nearly indistinguishable with a semblance of functionality and interface that mimics the genuine product. (Citation: Control Global May 2019) F-Secure Labs analyzed the approach the adversary used to compromise victim systems with Havex. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) The adversary planted trojanized software installers available on legitimate ICS/SCADA vendor websites. After being downloaded, this software infected the host computer with a Remote Access Trojan (RAT). MITRE source; not an assessment.
Note on B11: Adversaries may rely on a targeted organizations user interaction for the execution of malicious code. User interaction may consist of installing applications, opening email attachments, or granting higher permissions to documents. Adversaries may embed malicious code or visual basic code into files such as Microsoft Word and Excel documents or software installers. (Citation: Booz Allen Hamilton) Execution of this code requires that the user enable scripting or write access within the document. Embedded code may not always be noticeable to the user especially in cases of trojanized software. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012 delivered malware through spearphishing attachments which required user action to achieve execution. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) MITRE source; not an assessment.
Note on C11: Adversaries may steal the credentials of a specific user or service account using credential access techniques. In some cases, default credentials for control system devices may be publicly available. Compromised credentials may be used to bypass access controls placed on various resources on hosts and within the network, and may even be used for persistent access to remote systems. Compromised and default credentials may also grant an adversary increased privilege to specific systems and devices or access to restricted areas of the network. Adversaries may choose not to use malware or tools, in conjunction with the legitimate access those credentials provide, to make it harder to detect their presence or to control devices and send legitimate commands in an unintended way. Adversaries may also create accounts, sometimes using predefined account names and passwords, to provide a means of backup access for persistence. (Citation: Booz Allen Hamilton) The overlap of credentials and permissions across a network of systems is of concern because the adversary may be able to pivot across accounts and systems to reach a high level of access (i.e., domain or enterprise administrator) and possibly between the enterprise and operational technology environments. Adversaries may be able to leverage valid credentials from one system to gain access to another system. MITRE source; not an assessment.
Note on G11: Adversaries may leverage remote services to move between assets and network segments. These services are often used to allow operators to interact with systems remotely within the network, some examples are RDP, SMB, SSH, and other similar mechanisms. (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) (Citation: Dragos December 2017) (Citation: Joe Slowik April 2019) Remote services could be used to support remote access, data transmission, authentication, name resolution, and other remote functions. Further, remote services may be necessary to allow operators and administrators to configure systems within the network from their engineering or management workstations. An adversary may use this technique to access devices which may be dual-homed (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) to multiple network segments, and can be used for Program Download or to execute attacks on control devices directly through Valid Accounts. Specific remote services (RDP & VNC) may be a precursor to enable Graphical User Interface execution on devices such as HMIs or engineering workstation software. Based on incident data, CISA and FBI assessed that Chinese state-sponsored actors also compromised various authorized remote access channels, including systems designed to transfer data and/or allow access between corporate and ICS networks. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) MITRE source; not an assessment.
Note on H11: Adversaries may attempt to perform screen capture of devices in the control system environment. Screenshots may be taken of workstations, HMIs, or other devices that display environment-relevant process, device, reporting, alarm, or related data. These device displays may reveal information regarding the ICS process, layout, control, and related schematics. In particular, an HMI can provide a lot of important industrial process information. (Citation: ICS-CERT October 2017) Analysis of screen captures may provide the adversary with an understanding of intended operations and interactions between critical devices. MITRE source; not an assessment.
Note on J11: Adversaries may modify software and device credentials to prevent operator and responder access. Depending on the device, the modification or addition of this password could prevent any device configuration actions from being accomplished and may require a factory reset or replacement of hardware. These credentials are often built-in features provided by the device vendors as a means to restrict access to management interfaces. An adversary with access to valid or hardcoded credentials could change the credential to prevent future authorized device access. Change Credential may be especially damaging when paired with other techniques such as Modify Program, Data Destruction, or Modify Controller Tasking. In these cases, a device’s configuration may be destroyed or include malicious actions for the process environment, which cannot not be removed through normal device configuration actions. Additionally, recovery of the device and original configuration may be difficult depending on the features provided by the device. In some cases, these passwords cannot be removed onsite and may require that the device be sent back to the vendor for additional recovery steps. A chain of incidents occurred in Germany, where adversaries locked operators out of their building automation system (BAS) controllers by enabling a previously unset BCU key. (Citation: German BAS Lockout Dec 2021) MITRE source; not an assessment.
Note on L11: Adversaries may manipulate physical process control within the industrial environment. Methods of manipulating control can include changes to set point values, tags, or other parameters. Adversaries may manipulate control systems devices or possibly leverage their own, to communicate with and command physical control processes. The duration of manipulation may be temporary or longer sustained, depending on operator detection. Methods of Manipulation of Control include: * Man-in-the-middle * Spoof command message * Changing setpoints A Polish student used a remote controller device to interface with the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) (Citation: Bruce Schneier January 2008) Using this remote, the student was able to capture and replay legitimate tram signals. As a consequence, four trams were derailed and twelve people injured due to resulting emergency stops. (Citation: Shelley Smith February 2008) The track controlling commands issued may have also resulted in tram collisions, a further risk to those on board and nearby the areas of impact. (Citation: Bruce Schneier January 2008) MITRE source; not an assessment.
Note on A12: Adversaries may target devices that are transient across ICS networks and external networks. Normally, transient assets are brought into an environment by authorized personnel and do not remain in that environment on a permanent basis. (Citation: North American Electric Reliability Corporation June 2021) Transient assets are commonly needed to support management functions and may be more common in systems where a remotely managed asset is not feasible, external connections for remote access do not exist, or 3rd party contractor/vendor access is required. Adversaries may take advantage of transient assets in different ways. For instance, adversaries may target a transient asset when it is connected to an external network and then leverage its trusted access in another environment to launch an attack. They may also take advantage of installed applications and libraries that are used by legitimate end-users to interact with control system devices. Transient assets, in some cases, may not be deployed with a secure configuration leading to weaknesses that could allow an adversary to propagate malicious executable code, e.g., the transient asset may be infected by malware and when connected to an ICS environment the malware propagates onto other systems. MITRE source; not an assessment.
Note on G12: Adversaries may steal the credentials of a specific user or service account using credential access techniques. In some cases, default credentials for control system devices may be publicly available. Compromised credentials may be used to bypass access controls placed on various resources on hosts and within the network, and may even be used for persistent access to remote systems. Compromised and default credentials may also grant an adversary increased privilege to specific systems and devices or access to restricted areas of the network. Adversaries may choose not to use malware or tools, in conjunction with the legitimate access those credentials provide, to make it harder to detect their presence or to control devices and send legitimate commands in an unintended way. Adversaries may also create accounts, sometimes using predefined account names and passwords, to provide a means of backup access for persistence. (Citation: Booz Allen Hamilton) The overlap of credentials and permissions across a network of systems is of concern because the adversary may be able to pivot across accounts and systems to reach a high level of access (i.e., domain or enterprise administrator) and possibly between the enterprise and operational technology environments. Adversaries may be able to leverage valid credentials from one system to gain access to another system. MITRE source; not an assessment.
Note on H12: Adversaries may seek to capture radio frequency (RF) communication used for remote control and reporting in distributed environments. RF communication frequencies vary between 3 kHz to 300 GHz, although are commonly between 300 MHz to 6 GHz. (Citation: Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K. April 2018) The wavelength and frequency of the signal affect how the signal propagates through open air, obstacles (e.g. walls and trees) and the type of radio required to capture them. These characteristics are often standardized in the protocol and hardware and may have an effect on how the signal is captured. Some examples of wireless protocols that may be found in cyber-physical environments are: WirelessHART, Zigbee, WIA-FA, and 700 MHz Public Safety Spectrum. Adversaries may capture RF communications by using specialized hardware, such as software defined radio (SDR), handheld radio, or a computer with radio demodulator tuned to the communication frequency. (Citation: Bastille April 2017) Information transmitted over a wireless medium may be captured in-transit whether the sniffing device is the intended destination or not. This technique may be particularly useful to an adversary when the communications are not encrypted. (Citation: Gallagher, S. April 2017) In the 2017 Dallas Siren incident, it is suspected that adversaries likely captured wireless command message broadcasts on a 700 MHz frequency during a regular test of the system. These messages were later replayed to trigger the alarm systems. (Citation: Gallagher, S. April 2017) MITRE source; not an assessment.
Note on J12: Adversaries may perform data destruction over the course of an operation. The adversary may drop or create malware, tools, or other non-native files on a target system to accomplish this, potentially leaving behind traces of malicious activities. Such non-native files and other data may be removed over the course of an intrusion to maintain a small footprint or as a standard part of the post-intrusion cleanup process. (Citation: Enterprise ATT&CK January 2018) Data destruction may also be used to render operator interfaces unable to respond and to disrupt response functions from occurring as expected. An adversary may also destroy data backups that are vital to recovery after an incident. Standard file deletion commands are available on most operating system and device interfaces to perform cleanup, but adversaries may use other tools as well. Two examples are Windows Sysinternals SDelete and Active@ Killdisk. MITRE source; not an assessment.
Note on L12: Adversaries may attempt to manipulate the information reported back to operators or controllers. This manipulation may be short term or sustained. During this time the process itself could be in a much different state than what is reported. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) Operators may be fooled into doing something that is harmful to the system in a loss of view situation. With a manipulated view into the systems, operators may issue inappropriate control sequences that introduce faults or catastrophic failures into the system. Business analysis systems can also be provided with inaccurate data leading to bad management decisions. MITRE source; not an assessment.
Note on A13: Adversaries may perform wireless compromise as a method of gaining communications and unauthorized access to a wireless network. Access to a wireless network may be gained through the compromise of a wireless device. (Citation: Alexander Bolshev, Gleb Cherbov July 2014) (Citation: Alexander Bolshev March 2014) Adversaries may also utilize radios and other wireless communication devices on the same frequency as the wireless network. Wireless compromise can be done as an initial access vector from a remote distance. A Polish student used a modified TV remote controller to gain access to and control over the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) The remote controller device allowed the student to interface with the trams network to modify track settings and override operator control. The adversary may have accomplished this by aligning the controller to the frequency and amplitude of IR control protocol signals. (Citation: Bruce Schneier January 2008) The controller then enabled initial access to the network, allowing the capture and replay of tram signals. (Citation: John Bill May 2017) MITRE source; not an assessment.
Note on J13: Adversaries may perform Denial-of-Service (DoS) attacks to disrupt expected device functionality. Examples of DoS attacks include overwhelming the target device with a high volume of requests in a short time period and sending the target device a request it does not know how to handle. Disrupting device state may temporarily render it unresponsive, possibly lasting until a reboot can occur. When placed in this state, devices may be unable to send and receive requests, and may not perform expected response functions in reaction to other events in the environment. Some ICS devices are particularly sensitive to DoS events, and may become unresponsive in reaction to even a simple ping sweep. Adversaries may also attempt to execute a Permanent Denial-of-Service (PDoS) against certain devices, such as in the case of the BrickerBot malware. (Citation: ICS-CERT April 2017) Adversaries may exploit a software vulnerability to cause a denial of service by taking advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Vulnerabilities may exist in software that can be used to cause a denial of service condition. Adversaries may have prior knowledge about industrial protocols or control devices used in the environment through Remote System Information Discovery. There are examples of adversaries remotely causing a Device Restart/Shutdown by exploiting a vulnerability that induces uncontrolled resource consumption. (Citation: ICS-CERT August 2018) (Citation: Common Weakness Enumeration January 2019) (Citation: MITRE March 2018) MITRE source; not an assessment.
Note on L13: Adversaries may steal operational information on a production environment as a direct mission outcome for personal gain or to inform future operations. This information may include design documents, schedules, rotational data, or similar artifacts that provide insight on operations. In the Bowman Dam incident, adversaries probed systems for operational data. (Citation: Mark Thompson March 2016) (Citation: Danny Yadron December 2015) MITRE source; not an assessment.
Note on J14: Adversaries may forcibly restart or shutdown a device in an ICS environment to disrupt and potentially negatively impact physical processes. Methods of device restart and shutdown exist in some devices as built-in, standard functionalities. These functionalities can be executed using interactive device web interfaces, CLIs, and network protocol commands. Unexpected restart or shutdown of control system devices may prevent expected response functions happening during critical states. A device restart can also be a sign of malicious device modifications, as many updates require a shutdown in order to take effect. MITRE source; not an assessment.
Note on J15: Adversaries may manipulate the I/O image of PLCs through various means to prevent them from functioning as expected. Methods of I/O image manipulation may include overriding the I/O table via direct memory manipulation or using the override function used for testing PLC programs. (Citation: Dr. Kelvin T. Erickson December 2010) During the scan cycle, a PLC reads the status of all inputs and stores them in an image table. (Citation: Nanjundaiah, Vaidyanath) The image table is the PLCs internal storage location where values of inputs/outputs for one scan are stored while it executes the user program. After the PLC has solved the entire logic program, it updates the output image table. The contents of this output image table are written to the corresponding output points in I/O Modules. One of the unique characteristics of PLCs is their ability to override the status of a physical discrete input or to override the logic driving a physical output coil and force the output to a desired status. MITRE source; not an assessment.
Note on J16: Adversaries may modify alarm settings to prevent alerts that may inform operators of their presence or to prevent responses to dangerous and unintended scenarios. Reporting messages are a standard part of data acquisition in control systems. Reporting messages are used as a way to transmit system state information and acknowledgements that specific actions have occurred. These messages provide vital information for the management of a physical process, and keep operators, engineers, and administrators aware of the state of system devices and physical processes. If an adversary is able to change the reporting settings, certain events could be prevented from being reported. This type of modification can also prevent operators or devices from performing actions to keep the system in a safe state. If critical reporting messages cannot trigger these actions then a Impact could occur. In ICS environments, the adversary may have to use Alarm Suppression or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: Jos Wetzels, Marina Krotofil 2019) Methods of suppression often rely on modification of alarm settings, such as modifying in memory code to fixed values or tampering with assembly level instruction code. MITRE source; not an assessment.
Note on J17: Firmware is low-level software embedded in hardware that enables systems and devices to function properly and is commonly found in ICS environments. Adversaries may modify firmware on a system or device by installing malicious or vulnerable versions that enable them to achieve objectives such as Persistence, Impair Process Control, and Inhibit Response Function. Adversaries may modify system and device firmware by using the built-in firmware update functionality which may support local or remote installation. The malicious or vulnerable firmware may be delivered via Replication Through Removable Media, Supply Chain Compromise, or Remote Services. Once installed, the malicious or vulnerable firmware could be used to provide Rootkit and Hooking functionality, Exploitation for Privilege Escalation, or Denial of Service.(Citation: Basnight, Zachry, et al.) MITRE source; not an assessment.
Note on J18: System firmware on modern assets is often designed with an update feature. Older device firmware may be factory installed and require special reprograming equipment. When available, the firmware update feature enables vendors to remotely patch bugs and perform upgrades. Device firmware updates are often delegated to the user and may be done using a software update package. It may also be possible to perform this task over the network. An adversary may exploit the firmware update feature on accessible devices to upload malicious or out-of-date firmware. Malicious modification of device firmware may provide an adversary with root access to a device, given firmware is one of the lowest programming abstraction layers.(Citation: Basnight, Zachry, et al.) MITRE source; not an assessment.
Note on J19: Adversaries may install malicious or vulnerable firmware onto modular hardware devices. Control system devices often contain modular hardware devices. These devices may have their own set of firmware that is separate from the firmware of the main control system equipment. This technique is similar to System Firmware, but is conducted on other system components that may not have the same capabilities or level of integrity checking. Although it results in a device re-image, malicious device firmware may provide persistent access to remaining devices.(Citation: Daniel Peck, Dale Peterson January 2009) An easy point of access for an adversary is the Ethernet card, which may have its own CPU, RAM, and operating system. The adversary may attack and likely exploit the computer on an Ethernet card. Exploitation of the Ethernet card computer may enable the adversary to accomplish additional attacks, such as the following:(Citation: Daniel Peck, Dale Peterson January 2009) * Delayed Attack - The adversary may stage an attack in advance and choose when to launch it, such as at a particularly damaging time. * Brick the Ethernet Card - Malicious firmware may be programmed to result in an Ethernet card failure, requiring a factory return. * Random Attack or Failure - The adversary may load malicious firmware onto multiple field devices. Execution of an attack and the time it occurs is generated by a pseudo-random number generator. * A Field Device Worm - The adversary may choose to identify all field devices of the same model, with the end goal of performing a device-wide compromise. * Attack Other Cards on the Field Device - Although it is not the most important module in a field device, the Ethernet card is most accessible to the adversary and malware. Compromise of the Ethernet card may provide a more direct route to compromising other modules, such as the CPU module. MITRE source; not an assessment.
Note on J20: Adversaries may deploy rootkits to hide the presence of programs, files, network connections, services, drivers, and other system components. Rootkits are programs that hide the existence of malware by intercepting and modifying operating-system API calls that supply system information. Rootkits or rootkit-enabling functionality may reside at the user or kernel level in the operating system, or lower. (Citation: Enterprise ATT&CK January 2018) Firmware rootkits that affect the operating system yield nearly full control of the system. While firmware rootkits are normally developed for the main processing board, they can also be developed for the I/O that is attached to an asset. Compromise of this firmware allows the modification of all of the process variables and functions the module engages in. This may result in commands being disregarded and false information being fed to the main device. By tampering with device processes, an adversary may inhibit its expected response functions and possibly enable Impact. MITRE source; not an assessment.
Note on J21: Adversaries may stop or disable services on a system to render those services unavailable to legitimate users. Stopping critical services can inhibit or stop response to an incident or aid in the adversary's overall objectives to cause damage to the environment. (Citation: Enterprise ATT&CK) Services may not allow for modification of their data stores while running. Adversaries may stop services in order to conduct Data Destruction. (Citation: Enterprise ATT&CK) MITRE source; not an assessment.

## Embedded Matrix
Initial Access TA0108 | Execution TA0104 | Persistence TA0110 | Privilege Escalation TA0111 | Evasion TA0103 | Discovery TA0102 | Lateral Movement TA0109 | Collection TA0100 | Command and Control TA0101 | Inhibit Response Function TA0107 | Impair Process Control TA0106 | Impact TA0105
Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict.

## Windows Matrix
Initial Access TA0108 | Execution TA0104 | Persistence TA0110 | Privilege Escalation TA0111 | Evasion TA0103 | Discovery TA0102 | Lateral Movement TA0109 | Collection TA0100 | Command and Control TA0101 | Inhibit Response Function TA0107 | Impair Process Control TA0106 | Impact TA0105
Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict.

## Linux Matrix
Initial Access TA0108 | Execution TA0104 | Persistence TA0110 | Privilege Escalation TA0111 | Evasion TA0103 | Discovery TA0102 | Lateral Movement TA0109 | Collection TA0100 | Command and Control TA0101 | Inhibit Response Function TA0107 | Impair Process Control TA0106 | Impact TA0105
Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict.

## Network Devices Matrix
Initial Access TA0108 | Execution TA0104 | Persistence TA0110 | Privilege Escalation TA0111 | Evasion TA0103 | Discovery TA0102 | Lateral Movement TA0109 | Collection TA0100 | Command and Control TA0101 | Inhibit Response Function TA0107 | Impair Process Control TA0106 | Impact TA0105
Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict. | Not shown in this platform page; not an applicability verdict.

## View Comparison
View | Parents | Sub-techniques | Unique IDs | Directly tagged IDs | MITRE matrix
ICS | 79 | 18 | 97 | 97 | https://attack.mitre.org/versions/v19/matrices/ics/
Embedded | 0 | 0 | 0 | 0 | https://attack.mitre.org/versions/v19/matrices/ics/embedded/
Windows | 0 | 0 | 0 | 0 | https://attack.mitre.org/versions/v19/matrices/ics/windows/
Linux | 0 | 0 | 0 | 0 | https://attack.mitre.org/versions/v19/matrices/ics/linux/
Network Devices | 0 | 0 | 0 | 0 | https://attack.mitre.org/versions/v19/matrices/ics/network-devices/

## Technique Catalog
ID | Name | Parent ID | Tactics | Raw platforms | Website views | Targeted asset IDs | MITRE description | MITRE page | Object version | Modified
T0800 | Activate Firmware Update Mode |  | TA0107 | None | ICS | A0002; A0003; A0004; A0005; A0009; A0010; A0013; A0017; A0018 | Adversaries may activate firmware update mode on devices to prevent expected response functions from engaging in reaction to an emergency or process malfunction. For example, devices such as protection relays may have an operation mode designed for firmware installation. This mode may halt process monitoring and related functions to allow new firmware to be loaded. A device left in update mode may be placed in an inactive holding state if no firmware is provided to it. By entering and leaving a device in this mode, the adversary may deny its usual functionalities. | https://attack.mitre.org/versions/v19/techniques/T0800/ | 1.0 | 2026-05-12T15:12:00.622Z
T0801 | Monitor Process State |  | TA0100 | None | ICS | A0002; A0003; A0004; A0005; A0006; A0007; A0009; A0010; A0013; A0017; A0018 | Adversaries may gather information about the physical process state. This information may be used to gain more information about the process itself or used as a trigger for malicious actions. The sources of process state information may vary such as, OPC tags, historian data, specific PLC block information, or network traffic. | https://attack.mitre.org/versions/v19/techniques/T0801/ | 1.0 | 2025-04-25T15:16:45.982Z
T0802 | Automated Collection |  | TA0100 | None | ICS | A0003; A0006; A0007; A0017; A0018 | Adversaries may automate collection of industrial environment information using tools or scripts. This automated collection may leverage native control protocols and tools available in the control systems environment. For example, the OPC protocol may be used to enumerate and gather information. Access to a system or interface with these native protocols may allow collection and enumeration of other attached, communicating servers and devices. | https://attack.mitre.org/versions/v19/techniques/T0802/ | 1.1 | 2025-04-15T19:58:24.843Z
T0806 | Brute Force I/O |  | TA0106 | None | ICS | A0002; A0003; A0004; A0005; A0007; A0010; A0017; A0018 | Adversaries may repetitively or successively change I/O point values to perform an action. Brute Force I/O may be achieved by changing either a range of I/O point values or a single point value repeatedly to manipulate a process function. The adversary's goal and the information they have about the target environment will influence which of the options they choose. In the case of brute forcing a range of point values, the adversary may be able to achieve an impact without targeting a specific point. In the case where a single point is targeted, the adversary may be able to generate instability on the process function associated with that particular point. Adversaries may use Brute Force I/O to cause failures within various industrial processes. These failures could be the result of wear on equipment or damage to downstream equipment. | https://attack.mitre.org/versions/v19/techniques/T0806/ | 1.1 | 2025-04-16T21:26:16.573Z
T0807 | Command-Line Interface |  | TA0104 | None | ICS | A0001; A0002; A0006; A0007; A0008; A0009; A0012; A0015; A0016 | Adversaries may utilize command-line interfaces (CLIs) to interact with systems and execute commands. CLIs provide a means of interacting with computer systems and are a common feature across many types of platforms and devices within control systems environments. (Citation: Enterprise ATT&CK January 2018) Adversaries may also use CLIs to install and run new software, including malicious tools that may be installed over the course of an operation. CLIs are typically accessed locally, but can also be exposed via services, such as SSH, Telnet, and RDP. Commands that are executed in the CLI execute with the current permissions level of the process running the terminal emulator, unless the command specifies a change in permissions context. Many controllers have CLI interfaces for management purposes. | https://attack.mitre.org/versions/v19/techniques/T0807/ | 1.1 | 2026-05-12T15:12:00.623Z
T0809 | Data Destruction |  | TA0107 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Adversaries may perform data destruction over the course of an operation. The adversary may drop or create malware, tools, or other non-native files on a target system to accomplish this, potentially leaving behind traces of malicious activities. Such non-native files and other data may be removed over the course of an intrusion to maintain a small footprint or as a standard part of the post-intrusion cleanup process. (Citation: Enterprise ATT&CK January 2018) Data destruction may also be used to render operator interfaces unable to respond and to disrupt response functions from occurring as expected. An adversary may also destroy data backups that are vital to recovery after an incident. Standard file deletion commands are available on most operating system and device interfaces to perform cleanup, but adversaries may use other tools as well. Two examples are Windows Sysinternals SDelete and Active@ Killdisk. | https://attack.mitre.org/versions/v19/techniques/T0809/ | 1.0 | 2026-05-12T15:12:00.630Z
T0811 | Data from Information Repositories |  | TA0100 | None | ICS | A0006; A0007 | Adversaries may target and collect data from information repositories. This can include sensitive data such as specifications, schematics, or diagrams of control system layouts, devices, and processes. Examples of information repositories include reference databases in the process environment, as well as databases in the corporate network that might contain information about the ICS.(Citation: Cybersecurity & Infrastructure Security Agency March 2018) Information collected from these systems may provide the adversary with a better understanding of the operational environment, vendors used, processes, or procedures of the ICS. In a campaign between 2011 and 2013 against ONG organizations, Chinese state-sponsored actors searched document repositories for specific information such as, system manuals, remote terminal unit (RTU) sites, personnel lists, documents that included the string SCAD*, user credentials, and remote dial-up access information. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/versions/v19/techniques/T0811/ | 1.2 | 2025-04-16T21:26:13.205Z
T0813 | Denial of Control |  | TA0105 | None | ICS |  | Adversaries may cause a denial of control to temporarily prevent operators and engineers from interacting with process controls. An adversary may attempt to deny process control access to cause a temporary loss of communication with the control device or to prevent operator adjustment of process controls. An affected process may still be operating during the period of control loss, but not necessarily in a desired state. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) In the 2017 Dallas Siren incident operators were unable to disable the false alarms from the Office of Emergency Management headquarters. (Citation: Mark Loveless April 2017) | https://attack.mitre.org/versions/v19/techniques/T0813/ | 1.1 | 2025-04-15T19:59:15.775Z
T0814 | Denial of Service |  | TA0107 | None | ICS | A0002; A0003; A0004; A0005; A0006; A0007; A0009; A0010; A0012; A0013; A0015; A0016; A0017; A0018 | Adversaries may perform Denial-of-Service (DoS) attacks to disrupt expected device functionality. Examples of DoS attacks include overwhelming the target device with a high volume of requests in a short time period and sending the target device a request it does not know how to handle. Disrupting device state may temporarily render it unresponsive, possibly lasting until a reboot can occur. When placed in this state, devices may be unable to send and receive requests, and may not perform expected response functions in reaction to other events in the environment. Some ICS devices are particularly sensitive to DoS events, and may become unresponsive in reaction to even a simple ping sweep. Adversaries may also attempt to execute a Permanent Denial-of-Service (PDoS) against certain devices, such as in the case of the BrickerBot malware. (Citation: ICS-CERT April 2017) Adversaries may exploit a software vulnerability to cause a denial of service by taking advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Vulnerabilities may exist in software that can be used to cause a denial of service condition. Adversaries may have prior knowledge about industrial protocols or control devices used in the environment through Remote System Information Discovery. There are examples of adversaries remotely causing a Device Restart/Shutdown by exploiting a vulnerability that induces uncontrolled resource consumption. (Citation: ICS-CERT August 2018) (Citation: Common Weakness Enumeration January 2019) (Citation: MITRE March 2018) | https://attack.mitre.org/versions/v19/techniques/T0814/ | 1.1 | 2025-04-15T19:58:10.656Z
T0815 | Denial of View |  | TA0105 | None | ICS |  | Adversaries may cause a denial of view in attempt to disrupt and prevent operator oversight on the status of an ICS environment. This may manifest itself as a temporary communication failure between a device and its control source, where the interface recovers and becomes available once the interference ceases. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) An adversary may attempt to deny operator visibility by preventing them from receiving status and reporting messages. Denying this view may temporarily block and prevent operators from noticing a change in state or anomalous behavior. The environment's data and processes may still be operational, but functioning in an unintended or adversarial manner. | https://attack.mitre.org/versions/v19/techniques/T0815/ | 1.1 | 2025-04-15T19:58:33.142Z
T0816 | Device Restart/Shutdown |  | TA0107 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Adversaries may forcibly restart or shutdown a device in an ICS environment to disrupt and potentially negatively impact physical processes. Methods of device restart and shutdown exist in some devices as built-in, standard functionalities. These functionalities can be executed using interactive device web interfaces, CLIs, and network protocol commands. Unexpected restart or shutdown of control system devices may prevent expected response functions happening during critical states. A device restart can also be a sign of malicious device modifications, as many updates require a shutdown in order to take effect. | https://attack.mitre.org/versions/v19/techniques/T0816/ | 1.1 | 2026-05-12T15:12:00.623Z
T0817 | Drive-by Compromise |  | TA0108 | None | ICS | A0001 | Adversaries may gain access to a system during a drive-by compromise, when a user visits a website as part of a regular browsing session. With this technique, the user's web browser is targeted and exploited simply by visiting the compromised website. The adversary may target a specific community, such as trusted third party suppliers or other industry specific groups, which often visit the target website. This kind of targeted attack relies on a common interest, and is known as a strategic web compromise or watering hole attack. The National Cyber Awareness System (NCAS) has issued a Technical Alert (TA) regarding Russian government cyber activity targeting critical infrastructure sectors. (Citation: Cybersecurity & Infrastructure Security Agency March 2018) Analysis by DHS and FBI has noted two distinct categories of victims in the Dragonfly campaign on the Western energy sector: staging and intended targets. The adversary targeted the less secure networks of staging targets, including trusted third-party suppliers and related peripheral organizations. Initial access to the intended targets used watering hole attacks to target process control, ICS, and critical infrastructure related trade publications and informational websites. | https://attack.mitre.org/versions/v19/techniques/T0817/ | 1.0 | 2025-04-16T21:26:15.525Z
T0819 | Exploit Public-Facing Application |  | TA0108 | None | ICS | A0001; A0008; A0011; A0016 | Adversaries may leverage weaknesses to exploit internet-facing software for initial access into an industrial network. Internet-facing software may be user applications, underlying networking implementations, an assets operating system, weak defenses, etc. Targets of this technique may be intentionally exposed for the purpose of remote management and visibility. An adversary may seek to target public-facing applications as they may provide direct access into an ICS environment or the ability to move into the ICS network. Publicly exposed applications may be found through online tools that scan the internet for open ports and services. Version numbers for the exposed application may provide adversaries an ability to target specific known vulnerabilities. Exposed control protocol or remote access ports found in Commonly Used Port may be of interest by adversaries. | https://attack.mitre.org/versions/v19/techniques/T0819/ | 1.0 | 2025-04-16T21:26:13.044Z
T0820 | Exploitation for Evasion |  | TA0103 | None | ICS | A0001; A0002; A0003; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0014; A0015; A0016; A0017; A0018 | Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to evade detection. Vulnerabilities may exist in software that can be used to disable or circumvent security features. Adversaries may have prior knowledge through Remote System Information Discovery about security features implemented on control devices. These device security features will likely be targeted directly for exploitation. There are examples of firmware RAM/ROM consistency checks on control devices being targeted by adversaries to enable the installation of malicious System Firmware. | https://attack.mitre.org/versions/v19/techniques/T0820/ | 1.1 | 2025-04-16T21:26:16.960Z
T0821 | Modify Controller Tasking |  | TA0104 | None | ICS | A0003; A0010; A0017; A0018 | Adversaries may modify the tasking of a controller to allow for the execution of their own programs. This can allow an adversary to manipulate the execution flow and behavior of a controller. According to 61131-3, the association of a Task with a Program Organization Unit (POU) defines a task association. (Citation: IEC February 2013) An adversary may modify these associations or create new ones to manipulate the execution flow of a controller. Modification of controller tasking can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Tasks have properties, such as interval, frequency and priority to meet the requirements of program execution. Some controller vendors implement tasks with implicit, pre-defined properties whereas others allow for these properties to be formulated explicitly. An adversary may associate their program with tasks that have a higher priority or execute associated programs more frequently. For instance, to ensure cyclic execution of their program on a Siemens controller, an adversary may add their program to the task, Organization Block 1 (OB1). | https://attack.mitre.org/versions/v19/techniques/T0821/ | 1.2 | 2025-04-16T21:26:10.230Z
T0822 | External Remote Services |  | TA0108 | None | ICS | A0006; A0008; A0009; A0011; A0012; A0014; A0015; A0016; A0017 | Adversaries may leverage external remote services as a point of initial access into your network. These services allow users to connect to internal network resources from external locations. Examples are VPNs, Citrix, and other access mechanisms. Remote service gateways often manage connections and credential authentication for these services. (Citation: Daniel Oakley, Travis Smith, Tripwire) External remote services allow administration of a control system from outside the system. Often, vendors and internal engineering groups have access to external remote services to control system networks via the corporate network. In some cases, this access is enabled directly from the internet. While remote access enables ease of maintenance when a control system is in a remote area, compromise of remote access solutions is a liability. The adversary may use these services to gain access to and execute attacks against a control system network. Access to valid accounts is often a requirement. As they look for an entry point into the control system network, adversaries may begin searching for existing point-to-point VPN implementations at trusted third party networks or through remote support employee connections where split tunneling is enabled. (Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) | https://attack.mitre.org/versions/v19/techniques/T0822/ | 1.1 | 2026-05-12T15:12:00.705Z
T0823 | Graphical User Interface |  | TA0104 | None | ICS | A0001; A0002; A0006; A0007; A0008; A0009; A0012; A0015; A0016 | Adversaries may attempt to gain access to a machine via a Graphical User Interface (GUI) to enhance execution capabilities. Access to a GUI allows a user to interact with a computer in a more visual manner than a CLI. A GUI allows users to move a cursor and click on interface objects, with a mouse and keyboard as the main input devices, as opposed to just using the keyboard. If physical access is not an option, then access might be possible via protocols such as VNC on Linux-based and Unix-based operating systems, and RDP on Windows operating systems. An adversary can use this access to execute programs and applications on the target machine. | https://attack.mitre.org/versions/v19/techniques/T0823/ | 1.1 | 2026-05-12T15:12:00.707Z
T0826 | Loss of Availability |  | TA0105 | None | ICS |  | Adversaries may attempt to disrupt essential components or systems to prevent owner and operator from delivering products or services. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) Adversaries may leverage malware to delete or encrypt critical data on HMIs, workstations, or databases. In the 2021 Colonial Pipeline ransomware incident, pipeline operations were temporally halted on May 7th and were not fully restarted until May 12th. (Citation: Colonial Pipeline Company May 2021) | https://attack.mitre.org/versions/v19/techniques/T0826/ | 1.0 | 2025-04-15T19:59:00.088Z
T0827 | Loss of Control |  | TA0105 | None | ICS |  | Adversaries may seek to achieve a sustained loss of control or a runaway condition in which operators cannot issue any commands even if the malicious interference has subsided. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill in its 2014 IT Security Report.(Citation: BSI State of IT Security 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact resulted in damage and unsafe conditions from the uncontrolled shutdown of a blast furnace. | https://attack.mitre.org/versions/v19/techniques/T0827/ | 1.0 | 2026-05-12T15:12:00.706Z
T0828 | Loss of Productivity and Revenue |  | TA0105 | None | ICS |  | Adversaries may cause loss of productivity and revenue through disruption and even damage to the availability and integrity of control system operations, devices, and related processes. This technique may manifest as a direct effect of an ICS-targeting attack or tangentially, due to an IT-targeting attack against non-segregated environments. In cases where these operations or services are brought to a halt, the loss of productivity may eventually present an impact for the end-users or consumers of products and services. The disrupted supply-chain may result in supply shortages and increased prices, among other consequences. A ransomware attack on an Australian beverage company resulted in the shutdown of some manufacturing sites, including precautionary halts to protect key systems. (Citation: Paganini, Pierluigi June 2020) The company announced the potential for temporary shortages of their products following the attack. (Citation: Paganini, Pierluigi June 2020) (Citation: Lion Corporation June 2020) In the 2021 Colonial Pipeline ransomware incident, the pipeline was unable to transport approximately 2.5 million barrels of fuel per day to the East Coast. (Citation: Colonial Pipeline Company May 2021) | https://attack.mitre.org/versions/v19/techniques/T0828/ | 1.0 | 2025-04-16T21:26:15.157Z
T0829 | Loss of View |  | TA0105 | None | ICS |  | Adversaries may cause a sustained or permanent loss of view where the ICS equipment will require local, hands-on operator intervention; for instance, a restart or manual operation. By causing a sustained reporting or visibility loss, the adversary can effectively hide the present state of operations. This loss of view can occur without affecting the physical processes themselves. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) | https://attack.mitre.org/versions/v19/techniques/T0829/ | 1.0 | 2026-05-12T15:12:00.621Z
T0830 | Adversary-in-the-Middle |  | TA0100 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Adversaries with privileged network access may seek to modify network traffic in real time using adversary-in-the-middle (AiTM) attacks. (Citation: Gabriel Sanchez October 2017) This type of attack allows the adversary to intercept traffic to and/or from a particular device on the network. If a AiTM attack is established, then the adversary has the ability to block, log, modify, or inject traffic into the communication stream. There are several ways to accomplish this attack, but some of the most-common are Address Resolution Protocol (ARP) poisoning and the use of a proxy. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) An AiTM attack may allow an adversary to perform the following attacks: Block Reporting Message, Spoof Reporting Message, Modify Parameter, Unauthorized Command Message | https://attack.mitre.org/versions/v19/techniques/T0830/ | 2.0 | 2025-04-16T21:26:16.777Z
T0831 | Manipulation of Control |  | TA0105 | None | ICS |  | Adversaries may manipulate physical process control within the industrial environment. Methods of manipulating control can include changes to set point values, tags, or other parameters. Adversaries may manipulate control systems devices or possibly leverage their own, to communicate with and command physical control processes. The duration of manipulation may be temporary or longer sustained, depending on operator detection. Methods of Manipulation of Control include: * Man-in-the-middle * Spoof command message * Changing setpoints A Polish student used a remote controller device to interface with the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) (Citation: Bruce Schneier January 2008) Using this remote, the student was able to capture and replay legitimate tram signals. As a consequence, four trams were derailed and twelve people injured due to resulting emergency stops. (Citation: Shelley Smith February 2008) The track controlling commands issued may have also resulted in tram collisions, a further risk to those on board and nearby the areas of impact. (Citation: Bruce Schneier January 2008) | https://attack.mitre.org/versions/v19/techniques/T0831/ | 1.0 | 2025-04-16T21:26:10.752Z
T0832 | Manipulation of View |  | TA0105 | None | ICS |  | Adversaries may attempt to manipulate the information reported back to operators or controllers. This manipulation may be short term or sustained. During this time the process itself could be in a much different state than what is reported. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) Operators may be fooled into doing something that is harmful to the system in a loss of view situation. With a manipulated view into the systems, operators may issue inappropriate control sequences that introduce faults or catastrophic failures into the system. Business analysis systems can also be provided with inaccurate data leading to bad management decisions. | https://attack.mitre.org/versions/v19/techniques/T0832/ | 1.0 | 2025-04-15T19:58:29.210Z
T0834 | Native API |  | TA0104 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0015; A0016; A0017; A0018 | Adversaries may directly interact with the native OS application programming interface (API) to access system functions. Native APIs provide a controlled means of calling low-level OS services within the kernel, such as those involving hardware/devices, memory, and processes. (Citation: The MITRE Corporation May 2017) These native APIs are leveraged by the OS during system boot (when other system components are not yet initialized) as well as carrying out tasks and requests during routine operations. Functionality provided by native APIs are often also exposed to user-mode applications via interfaces and libraries. For example, functions such as memcpy and direct operations on memory registers can be used to modify user and system memory space. | https://attack.mitre.org/versions/v19/techniques/T0834/ | 1.0 | 2025-04-16T21:26:17.499Z
T0835 | Manipulate I/O Image |  | TA0107 | None | ICS | A0003; A0010; A0017; A0018 | Adversaries may manipulate the I/O image of PLCs through various means to prevent them from functioning as expected. Methods of I/O image manipulation may include overriding the I/O table via direct memory manipulation or using the override function used for testing PLC programs. (Citation: Dr. Kelvin T. Erickson December 2010) During the scan cycle, a PLC reads the status of all inputs and stores them in an image table. (Citation: Nanjundaiah, Vaidyanath) The image table is the PLCs internal storage location where values of inputs/outputs for one scan are stored while it executes the user program. After the PLC has solved the entire logic program, it updates the output image table. The contents of this output image table are written to the corresponding output points in I/O Modules. One of the unique characteristics of PLCs is their ability to override the status of a physical discrete input or to override the logic driving a physical output coil and force the output to a desired status. | https://attack.mitre.org/versions/v19/techniques/T0835/ | 1.1 | 2025-04-15T19:58:22.225Z
T0836 | Modify Parameter |  | TA0106 | None | ICS | A0003; A0004; A0005; A0017; A0018 | Adversaries may modify parameters used to instruct industrial control system devices. These devices operate via programs that dictate how and when to perform actions based on such parameters. Such parameters can determine the extent to which an action is performed and may specify additional options. For example, a program on a control system device dictating motor processes may take a parameter defining the total number of seconds to run that motor. An adversary can potentially modify these parameters to produce an outcome outside of what was intended by the operators. By modifying system and process critical parameters, the adversary may cause Impact to equipment and/or control processes. Modified parameters may be turned into dangerous, out-of-bounds, or unexpected values from typical operations. For example, specifying that a process run for more or less time than it should, or dictating an unusually high, low, or invalid value as a parameter. | https://attack.mitre.org/versions/v19/techniques/T0836/ | 1.3 | 2025-04-16T21:26:10.077Z
T0837 | Loss of Protection |  | TA0105 | None | ICS |  | Adversaries may compromise protective system functions designed to prevent the effects of faults and abnormal conditions. This can result in equipment damage, prolonged process disruptions and hazards to personnel. Many faults and abnormal conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable protective system functions as a prerequisite to subsequent attack execution or to allow for future faults and abnormal conditions to go unchecked. Detection of a Loss of Protection by operators can result in the shutdown of a process due to strict policies regarding protection systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. | https://attack.mitre.org/versions/v19/techniques/T0837/ | 1.0 | 2025-04-16T21:26:12.172Z
T0838 | Modify Alarm Settings |  | TA0107 | None | ICS | A0002; A0003; A0004; A0005; A0009; A0010; A0017; A0018 | Adversaries may modify alarm settings to prevent alerts that may inform operators of their presence or to prevent responses to dangerous and unintended scenarios. Reporting messages are a standard part of data acquisition in control systems. Reporting messages are used as a way to transmit system state information and acknowledgements that specific actions have occurred. These messages provide vital information for the management of a physical process, and keep operators, engineers, and administrators aware of the state of system devices and physical processes. If an adversary is able to change the reporting settings, certain events could be prevented from being reported. This type of modification can also prevent operators or devices from performing actions to keep the system in a safe state. If critical reporting messages cannot trigger these actions then a Impact could occur. In ICS environments, the adversary may have to use Alarm Suppression or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: Jos Wetzels, Marina Krotofil 2019) Methods of suppression often rely on modification of alarm settings, such as modifying in memory code to fixed values or tampering with assembly level instruction code. | https://attack.mitre.org/versions/v19/techniques/T0838/ | 1.2 | 2026-05-12T15:12:00.723Z
T0840 | Network Connection Enumeration |  | TA0102 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0015; A0016; A0017; A0018 | Adversaries may perform network connection enumeration to discover information about device communication patterns. If an adversary can inspect the state of a network connection with tools, such as Netstat(Citation: Netstat), in conjunction with System Firmware, then they can determine the role of certain devices on the network (Citation: MITRE). The adversary can also use Network Sniffing to watch network traffic for details about the source, destination, protocol, and content. | https://attack.mitre.org/versions/v19/techniques/T0840/ | 1.2 | 2026-05-12T15:12:00.723Z
T0842 | Network Sniffing |  | TA0102 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0015; A0016; A0017; A0018 | Network sniffing is the practice of using a network interface on a computer system to monitor or capture information (Citation: Enterprise ATT&CK January 2018) regardless of whether it is the specified destination for the information. An adversary may attempt to sniff the traffic to gain information about the target. This information can vary in the level of importance. Relatively unimportant information is general communications to and from machines. Relatively important information would be login information. User credentials may be sent over an unencrypted protocol, such as Telnet, that can be captured and obtained through network packet analysis. In addition, ARP and Domain Name Service (DNS) poisoning can be used to capture credentials to websites, proxies, and internal systems by redirecting traffic to an adversary. | https://attack.mitre.org/versions/v19/techniques/T0842/ | 1.0 | 2025-04-16T21:26:13.380Z
T0843 | Program Download |  | TA0109 | None | ICS | A0003; A0010; A0017; A0018 | Adversaries may perform a program download to transfer a user program to a controller. Variations of program download, such as online edit and program append, allow a controller to continue running during the transfer and reconfiguration process without interruption to process control. However, before starting a full program download (i.e., download all) a controller may need to go into a stop state. This can have negative consequences on the physical process, especially if the controller is not able to fulfill a time-sensitive action. Adversaries may choose to avoid a download all in favor of an online edit or program append to avoid disrupting the physical process. An adversary may need to use the technique Detect Operating Mode or Change Operating Mode to make sure the controller is in the proper mode to accept a program download. The granularity of control to transfer a user program in whole or parts is dictated by the management protocol (e.g., S7CommPlus, TriStation) and underlying controller API. Thus, program download is a high-level term for the suite of vendor-specific API calls used to configure a controllers user program memory space. Modify Controller Tasking and Modify Program represent the configuration changes that are transferred to a controller via a program download. | https://attack.mitre.org/versions/v19/techniques/T0843/ | 1.1 | 2026-05-12T15:12:00.713Z
T0843.001 | Download All | T0843 | TA0109 | [field absent] | ICS | A0003; A0010; A0017; A0018 | Adversaries may execute a full program download to a PLC to overwrite the entire PLC program and configuration to deploy a new project or make major changes. This typically requires stopping the PLC and adversely impacting control processes. The ability to perform a full program download to the PLC typically relies on access to a workstation with the vendor-specific PLC programming software installed. | https://attack.mitre.org/versions/v19/techniques/T0843/001/ | 1.0 | 2026-05-12T15:12:00.642Z
T0843.002 | Online Edit | T0843 | TA0109 | [field absent] | ICS | A0003; A0010; A0017; A0018 | Adversaries may execute an online edit of a PLC to update parts of an existing program. It does not require stopping the PLC which allows it to continue running during transfer and reconfiguration without interruption to process control. Adversaries may leverage this approach to minimize downtime and evade detection. The ability to perform an online edit to the PLC typically relies on access to a workstation with the vendor-specific PLC programming software installed. | https://attack.mitre.org/versions/v19/techniques/T0843/002/ | 1.0 | 2026-05-12T15:12:00.721Z
T0843.003 | Program Append | T0843 | TA0109 | [field absent] | ICS | A0003; A0010; A0017; A0018 | Adversaries may execute a program append to a PLC to update parts of an existing program. It may or may not require stopping the PLC which may allow it to continue running during transfer and reconfiguration without interruption to process control. Adversaries may leverage this approach to minimize downtime and evade detection. The ability to perform a program append to the PLC typically relies on access to a workstation with the vendor-specific PLC programming software installed. | https://attack.mitre.org/versions/v19/techniques/T0843/003/ | 1.0 | 2026-05-12T15:12:00.634Z
T0845 | Program Upload |  | TA0100 | None | ICS | A0003; A0010; A0017; A0018 | Adversaries may attempt to upload a program from a PLC to gather information about an industrial process. Uploading a program may allow them to acquire and study the underlying logic. Methods of program upload include vendor software, which enables the user to upload and read a program running on a PLC. This software can be used to upload the target program to a workstation, jump box, or an interfacing device. | https://attack.mitre.org/versions/v19/techniques/T0845/ | 1.0 | 2025-04-25T15:16:46.293Z
T0846 | Remote System Discovery |  | TA0102 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0015; A0016; A0017; A0018 | Adversaries may attempt to get a listing of other systems by IP address, hostname, or other logical identifier on a network that may be used for subsequent Lateral Movement or Discovery techniques. Functionality could exist within adversary tools to enable this, but utilities available on the operating system or vendor software could also be used.(Citation: Enterprise ATT&CK January 2018) | https://attack.mitre.org/versions/v19/techniques/T0846/ | 1.1 | 2026-05-12T15:12:00.718Z
T0846.001 | Port Scan | T0846 | TA0102 | [field absent] | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0014; A0015; A0016; A0017; A0018 | Adversaries may perform a port scan on a system, device, or network to identify live hosts, enumerate open ports and running services, identify operating systems, and map out the network.(Citation: NIST SP 800-82r3) The results of a port scan may inform adversary Discovery, Lateral Movement, and vulnerability exploitation decisions (Exploitation for Evasion, Exploitation for Privilege Escalation, Exploitation of Remote Services). Some common tools for executing a port scan include nmap, netcat, and the Advanced Port Scanner. | https://attack.mitre.org/versions/v19/techniques/T0846/001/ | 1.0 | 2026-05-12T15:12:00.635Z
T0846.002 | Broadcast Discovery | T0846 | TA0102 | [field absent] | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0014; A0015; A0016; A0017; A0018 | Adversaries may perform broadcast discovery requests to enumerate systems and devices on a network. Broadcast discovery works by one system or device sending messages to all systems and devices on a network (or subnet) and then waiting for a response. If a response is received that means the system or device that responded is live and can communicate over that protocol. Adversaries may leverage different protocols supported on the network for sending broadcast messages. Some common OT protocols that have broadcast discovery mechanisms are Building Automation and Control Network (BACNet) Who-Is requests, Common Industrial Protocol (CIP) List Identity User Datagram Protocol (UDP) broadcast requests, and Siemens S7 broadcast identification requests.(Citation: Broadcasting BACnet)(Citation: Cisco Active Discovery) | https://attack.mitre.org/versions/v19/techniques/T0846/002/ | 1.0 | 2026-05-12T15:12:00.714Z
T0846.003 | Multicast Discovery | T0846 | TA0102 | [field absent] | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0014; A0015; A0016; A0017; A0018 | Adversaries may perform multicast discovery requests which is when one system or device sends messages to all systems and devices in a pre-defined group on a network (or subnet) and then waits for a response. If a response is received that means the system or device that responded is live and can communicate over that protocol. Multicast discovery tends to be stealthier than broadcast discovery because every system or device on the network (or subnet) is not being messaged. One common OT protocol that has a multicast discovery mechanism is the Process Field Network (PROFINET) Discovery and Configuration Protocol (DCP) with its Identify All requests.(Citation: Cisco Active Discovery) | https://attack.mitre.org/versions/v19/techniques/T0846/003/ | 1.0 | 2026-05-12T15:12:00.636Z
T0847 | Replication Through Removable Media |  | TA0108 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0017; A0018 | Adversaries may move onto systems, such as those separated from the enterprise network, by copying malware to removable media which is inserted into the control systems environment. The adversary may rely on unknowing trusted third parties, such as suppliers or contractors with access privileges, to introduce the removable media. This technique enables initial access to target devices that never connect to untrusted networks, but are physically accessible. Operators of the German nuclear power plant, Gundremmingen, discovered malware on a facility computer not connected to the internet. (Citation: Kernkraftwerk Gundremmingen April 2016) (Citation: Trend Micro April 2016) The malware included Conficker and W32.Ramnit, which were also found on eighteen removable disk drives in the facility. (Citation: Christoph Steitz, Eric Auchard April 2016) (Citation: Catalin Cimpanu April 2016) (Citation: Peter Dockrill April 2016) (Citation: Lee Mathews April 2016) (Citation: Sean Gallagher April 2016) (Citation: Dark Reading Staff April 2016) The plant has since checked for infection and cleaned up more than 1,000 computers. (Citation: BBC April 2016) An ESET researcher commented that internet disconnection does not guarantee system safety from infection or payload execution. (Citation: ESET April 2016) | https://attack.mitre.org/versions/v19/techniques/T0847/ | 1.0 | 2025-04-15T19:59:04.946Z
T0848 | Rogue Master |  | TA0108 | None | ICS | A0002; A0003; A0004; A0005; A0006; A0007; A0009; A0010; A0017; A0018 | Adversaries may setup a rogue master to leverage control server functions to communicate with outstations. A rogue master can be used to send legitimate control messages to other control system devices, affecting processes in unintended ways. It may also be used to disrupt network communications by capturing and receiving the network traffic meant for the actual master. Impersonating a master may also allow an adversary to avoid detection. In the case of the 2017 Dallas Siren incident, adversaries used a rogue master to send command messages to the 156 distributed sirens across the city, either through a single rogue transmitter with a strong signal, or using many distributed repeaters. (Citation: Bastille April 2017) (Citation: Zack Whittaker April 2017) | https://attack.mitre.org/versions/v19/techniques/T0848/ | 1.2 | 2025-04-16T21:26:17.326Z
T0849 | Masquerading |  | TA0103 | None | ICS | A0001; A0002; A0006; A0007; A0008; A0009; A0012 | Adversaries may use masquerading to disguise a malicious application or executable as another file, to avoid operator and engineer suspicion. Possible disguises of these masquerading files can include commonly found programs, expected vendor executables and configuration files, and other commonplace application and naming conventions. By impersonating expected and vendor-relevant files and applications, operators and engineers may not notice the presence of the underlying malicious content and possibly end up running those masquerading as legitimate functions. Applications and other files commonly found on Windows systems or in engineering workstations have been impersonated before. This can be as simple as renaming a file to effectively disguise it in the ICS environment. | https://attack.mitre.org/versions/v19/techniques/T0849/ | 1.1 | 2025-04-16T21:26:18.036Z
T0851 | Rootkit |  | TA0103; TA0107 | None | ICS | A0001; A0002; A0003; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0015; A0016; A0017; A0018 | Adversaries may deploy rootkits to hide the presence of programs, files, network connections, services, drivers, and other system components. Rootkits are programs that hide the existence of malware by intercepting and modifying operating-system API calls that supply system information. Rootkits or rootkit-enabling functionality may reside at the user or kernel level in the operating system, or lower. (Citation: Enterprise ATT&CK January 2018) Firmware rootkits that affect the operating system yield nearly full control of the system. While firmware rootkits are normally developed for the main processing board, they can also be developed for the I/O that is attached to an asset. Compromise of this firmware allows the modification of all of the process variables and functions the module engages in. This may result in commands being disregarded and false information being fed to the main device. By tampering with device processes, an adversary may inhibit its expected response functions and possibly enable Impact. | https://attack.mitre.org/versions/v19/techniques/T0851/ | 1.1 | 2025-04-16T21:26:13.542Z
T0852 | Screen Capture |  | TA0100 | None | ICS | A0001; A0002; A0012 | Adversaries may attempt to perform screen capture of devices in the control system environment. Screenshots may be taken of workstations, HMIs, or other devices that display environment-relevant process, device, reporting, alarm, or related data. These device displays may reveal information regarding the ICS process, layout, control, and related schematics. In particular, an HMI can provide a lot of important industrial process information. (Citation: ICS-CERT October 2017) Analysis of screen captures may provide the adversary with an understanding of intended operations and interactions between critical devices. | https://attack.mitre.org/versions/v19/techniques/T0852/ | 1.0 | 2026-05-12T15:12:00.715Z
T0853 | Scripting |  | TA0104 | None | ICS | A0001; A0002; A0006; A0007; A0008; A0009; A0012; A0015; A0016 | Adversaries may use scripting languages to execute arbitrary code in the form of a pre-written script or in the form of user-supplied code to an interpreter. Scripting languages are programming languages that differ from compiled languages, in that scripting languages use an interpreter, instead of a compiler. These interpreters read and compile part of the source code just before it is executed, as opposed to compilers, which compile each and every line of code to an executable file. Scripting allows software developers to run their code on any system where the interpreter exists. This way, they can distribute one package, instead of precompiling executables for many different systems. Scripting languages, such as Python, have their interpreters shipped as a default with many Linux distributions. In addition to being a useful tool for developers and administrators, scripting language interpreters may be abused by the adversary to execute code in the target environment. Due to the nature of scripting languages, this allows for weaponized code to be deployed to a target easily, and leaves open the possibility of on-the-fly scripting to perform a task. | https://attack.mitre.org/versions/v19/techniques/T0853/ | 1.0 | 2025-04-16T21:26:12.511Z
T0858 | Change Operating Mode |  | TA0104; TA0103 | None | ICS | A0003; A0010; A0017; A0018 | Adversaries may change the operating mode of a controller to gain additional access to engineering functions such as Program Download. Programmable controllers typically have several modes of operation that control the state of the user program and control access to the controllers API. Operating modes can be physically selected using a key switch on the face of the controller but may also be selected with calls to the controllers API. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: * Program - This mode must be enabled before changes can be made to a devices program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLCs logic Is halted, and all outputs may be forced off. (Citation: N.A. October 2017) * Run - Execution of the devices program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the programs logic. Program Upload and Program Download are disabled while in this mode. (Citation: Omron) (Citation: Machine Information Systems 2007) (Citation: N.A. October 2017) (Citation: PLCgurus 2021) * Remote - Allows for remote changes to a PLCs operation mode. (Citation: PLCgurus 2021) * Stop - The PLC and program is stopped, while in this mode, outputs are forced off. (Citation: Machine Information Systems 2007) * Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. (Citation: Machine Information Systems 2007) * Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. (Citation: Omron) | https://attack.mitre.org/versions/v19/techniques/T0858/ | 1.0 | 2026-05-12T15:12:00.623Z
T0859 | Valid Accounts |  | TA0110; TA0109 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0015; A0016; A0017; A0018 | Adversaries may steal the credentials of a specific user or service account using credential access techniques. In some cases, default credentials for control system devices may be publicly available. Compromised credentials may be used to bypass access controls placed on various resources on hosts and within the network, and may even be used for persistent access to remote systems. Compromised and default credentials may also grant an adversary increased privilege to specific systems and devices or access to restricted areas of the network. Adversaries may choose not to use malware or tools, in conjunction with the legitimate access those credentials provide, to make it harder to detect their presence or to control devices and send legitimate commands in an unintended way. Adversaries may also create accounts, sometimes using predefined account names and passwords, to provide a means of backup access for persistence. (Citation: Booz Allen Hamilton) The overlap of credentials and permissions across a network of systems is of concern because the adversary may be able to pivot across accounts and systems to reach a high level of access (i.e., domain or enterprise administrator) and possibly between the enterprise and operational technology environments. Adversaries may be able to leverage valid credentials from one system to gain access to another system. | https://attack.mitre.org/versions/v19/techniques/T0859/ | 1.1 | 2026-05-12T15:12:00.717Z
T0860 | Wireless Compromise |  | TA0108 | None | ICS | A0001; A0013 | Adversaries may perform wireless compromise as a method of gaining communications and unauthorized access to a wireless network. Access to a wireless network may be gained through the compromise of a wireless device. (Citation: Alexander Bolshev, Gleb Cherbov July 2014) (Citation: Alexander Bolshev March 2014) Adversaries may also utilize radios and other wireless communication devices on the same frequency as the wireless network. Wireless compromise can be done as an initial access vector from a remote distance. A Polish student used a modified TV remote controller to gain access to and control over the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) The remote controller device allowed the student to interface with the trams network to modify track settings and override operator control. The adversary may have accomplished this by aligning the controller to the frequency and amplitude of IR control protocol signals. (Citation: Bruce Schneier January 2008) The controller then enabled initial access to the network, allowing the capture and replay of tram signals. (Citation: John Bill May 2017) | https://attack.mitre.org/versions/v19/techniques/T0860/ | 1.2 | 2025-04-15T19:58:15.610Z
T0861 | Point & Tag Identification |  | TA0100 | None | ICS | A0002; A0003; A0004; A0005; A0006; A0007; A0009; A0010; A0017; A0018 | Adversaries may collect point and tag values to gain a more comprehensive understanding of the process environment. Points may be values such as inputs, memory locations, outputs or other process specific variables. (Citation: Dennis L. Sloatman September 2016) Tags are the identifiers given to points for operator convenience. Collecting such tags provides valuable context to environmental points and enables an adversary to map inputs, outputs, and other values to their control processes. Understanding the points being collected may inform an adversary on which processes and values to keep track of over the course of an operation. | https://attack.mitre.org/versions/v19/techniques/T0861/ | 1.1 | 2025-04-16T21:26:11.231Z
T0862 | Supply Chain Compromise |  | TA0108 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0015; A0016; A0017; A0018 | Adversaries may perform supply chain compromise to gain control systems environment access by means of infected products, software, and workflows. Supply chain compromise is the manipulation of products, such as devices or software, or their delivery mechanisms before receipt by the end consumer. Adversary compromise of these products and mechanisms is done for the goal of data or system compromise, once infected products are introduced to the target environment. Supply chain compromise can occur at all stages of the supply chain, from manipulation of development tools and environments to manipulation of developed products and tools distribution mechanisms. This may involve the compromise and replacement of legitimate software and patches, such as on third party or vendor websites. Targeting of supply chain compromise can be done in attempts to infiltrate the environments of a specific audience. In control systems environments with assets in both the IT and OT networks, it is possible a supply chain compromise affecting the IT environment could enable further access to the OT environment. Counterfeit devices may be introduced to the global supply chain posing safety and cyber risks to asset owners and operators. These devices may not meet the safety, engineering and manufacturing requirements of regulatory bodies but may feature tagging indicating conformance with industry standards. Due to the lack of adherence to standards and overall lesser quality, the counterfeit products may pose a serious safety and operational risk. (Citation: Control Global May 2019) Yokogawa identified instances in which their customers received counterfeit differential pressure transmitters using the Yokogawa logo. The counterfeit transmitters were nearly indistinguishable with a semblance of functionality and interface that mimics the genuine product. (Citation: Control Global May 2019) F-Secure Labs analyzed the approach the adversary used to compromise victim systems with Havex. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) The adversary planted trojanized software installers available on legitimate ICS/SCADA vendor websites. After being downloaded, this software infected the host computer with a Remote Access Trojan (RAT). | https://attack.mitre.org/versions/v19/techniques/T0862/ | 1.1 | 2025-04-16T21:26:14.822Z
T0863 | User Execution |  | TA0104 | None | ICS | A0001; A0002; A0012 | Adversaries may rely on a targeted organizations user interaction for the execution of malicious code. User interaction may consist of installing applications, opening email attachments, or granting higher permissions to documents. Adversaries may embed malicious code or visual basic code into files such as Microsoft Word and Excel documents or software installers. (Citation: Booz Allen Hamilton) Execution of this code requires that the user enable scripting or write access within the document. Embedded code may not always be noticeable to the user especially in cases of trojanized software. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012 delivered malware through spearphishing attachments which required user action to achieve execution. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/versions/v19/techniques/T0863/ | 1.1 | 2025-04-15T19:58:15.054Z
T0864 | Transient Cyber Asset |  | TA0108 | None | ICS | A0001 | Adversaries may target devices that are transient across ICS networks and external networks. Normally, transient assets are brought into an environment by authorized personnel and do not remain in that environment on a permanent basis. (Citation: North American Electric Reliability Corporation June 2021) Transient assets are commonly needed to support management functions and may be more common in systems where a remotely managed asset is not feasible, external connections for remote access do not exist, or 3rd party contractor/vendor access is required. Adversaries may take advantage of transient assets in different ways. For instance, adversaries may target a transient asset when it is connected to an external network and then leverage its trusted access in another environment to launch an attack. They may also take advantage of installed applications and libraries that are used by legitimate end-users to interact with control system devices. Transient assets, in some cases, may not be deployed with a secure configuration leading to weaknesses that could allow an adversary to propagate malicious executable code, e.g., the transient asset may be infected by malware and when connected to an ICS environment the malware propagates onto other systems. | https://attack.mitre.org/versions/v19/techniques/T0864/ | 1.2 | 2025-04-15T19:58:21.226Z
T0865 | Spearphishing Attachment |  | TA0108 | None | ICS | A0001; A0012 | Adversaries may use a spearphishing attachment, a variant of spearphishing, as a form of a social engineering attack against specific targets. Spearphishing attachments are different from other forms of spearphishing in that they employ malware attached to an email. All forms of spearphishing are electronically delivered and target a specific individual, company, or industry. In this scenario, adversaries attach a file to the spearphishing email and usually rely upon User Execution to gain execution and access. (Citation: Enterprise ATT&CK October 2019) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012, targeted ONG organizations and their employees. The emails were constructed with a high level of sophistication to convince employees to open the malicious file attachments. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/versions/v19/techniques/T0865/ | 1.1 | 2025-04-16T21:26:15.346Z
T0866 | Exploitation of Remote Services |  | TA0108; TA0109 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0014; A0015; A0016; A0017; A0018 | Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to enable remote service abuse. A common goal for post-compromise exploitation of remote services is for initial access into and lateral movement throughout the ICS environment to enable access to targeted systems. (Citation: Enterprise ATT&CK) ICS asset owners and operators have been affected by ransomware (or disruptive malware masquerading as ransomware) migrating from enterprise IT to ICS environments: WannaCry, NotPetya, and BadRabbit. In each of these cases, self-propagating (wormable) malware initially infected IT networks, but through exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks, producing significant impacts. (Citation: Joe Slowik April 2019) | https://attack.mitre.org/versions/v19/techniques/T0866/ | 1.0 | 2025-04-16T21:26:16.054Z
T0867 | Lateral Tool Transfer |  | TA0109 | None | ICS | A0001; A0007; A0008; A0011; A0012; A0013 | Adversaries may transfer tools or other files from one system to another to stage adversary tools or other files over the course of an operation. (Citation: Enterprise ATT&CK) Copying of files may also be performed laterally between internal victim systems to support Lateral Movement with remote Execution using inherent file sharing protocols such as file sharing over SMB to connected network shares. (Citation: Enterprise ATT&CK) In control systems environments, malware may use SMB and other file sharing protocols to move laterally through industrial networks. | https://attack.mitre.org/versions/v19/techniques/T0867/ | 1.1 | 2025-04-16T21:26:20.126Z
T0868 | Detect Operating Mode |  | TA0100 | None | ICS | A0003; A0010; A0017; A0018 | Adversaries may gather information about a PLCs or controllers current operating mode. Operating modes dictate what change or maintenance functions can be manipulated and are often controlled by a key switch on the PLC (e.g., run, prog [program], and remote). Knowledge of these states may be valuable to an adversary to determine if they are able to reprogram the PLC. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: * Program - This mode must be enabled before changes can be made to a devices program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLCs logic Is halted, and all outputs may be forced off. (Citation: N.A. October 2017) * Run - Execution of the devices program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the programs logic.Program Upload and Program Download are disabled while in this mode. (Citation: Omron) (Citation: Machine Information Systems 2007) (Citation: N.A. October 2017) (Citation: PLCgurus 2021) * Remote - Allows for remote changes to a PLCs operation mode. (Citation: PLCgurus 2021) * Stop - The PLC and program is stopped, while in this mode, outputs are forced off. (Citation: Machine Information Systems 2007) * Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. (Citation: Machine Information Systems 2007) * Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. (Citation: Omron) | https://attack.mitre.org/versions/v19/techniques/T0868/ | 1.0 | 2025-04-16T21:26:11.972Z
T0869 | Standard Application Layer Protocol |  | TA0101 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0015; A0016; A0017; A0018 | Adversaries may establish command and control capabilities over commonly used application layer protocols such as HTTP(S), OPC, RDP, telnet, DNP3, and modbus. These protocols may be used to disguise adversary actions as benign network traffic. Standard protocols may be seen on their associated port or in some cases over a non-standard port. Adversaries may use these protocols to reach out of the network for command and control, or in some cases to other infected devices within the network. | https://attack.mitre.org/versions/v19/techniques/T0869/ | 1.0 | 2025-04-25T15:16:52.173Z
T0871 | Execution through API |  | TA0104 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0009; A0010; A0013; A0015; A0016; A0017; A0018 | Adversaries may attempt to leverage Application Program Interfaces (APIs) used for communication between control software and the hardware. Specific functionality is often coded into APIs which can be called by software to engage specific functions on a device or other software. | https://attack.mitre.org/versions/v19/techniques/T0871/ | 1.1 | 2025-04-16T21:26:14.643Z
T0872 | Indicator Removal on Host |  | TA0103 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0015; A0016; A0017; A0018 | Adversaries may attempt to remove indicators of their presence on a system in an effort to cover their tracks. In cases where an adversary may feel detection is imminent, they may try to overwrite, delete, or cover up changes they have made to the device. | https://attack.mitre.org/versions/v19/techniques/T0872/ | 1.0 | 2025-04-25T15:16:47.841Z
T0873 | Project File Infection |  | TA0110 | None | ICS | A0001 | Adversaries may attempt to infect project files with malicious code. These project files may consist of objects, program organization units, variables such as tags, documentation, and other configurations needed for PLC programs to function.(Citation: Beckhoff) Using built in functions of the engineering software, adversaries may be able to download an infected program to a PLC in the operating environment enabling further Execution and Persistence techniques.(Citation: PLCdev) Adversaries may export their own code into project files with conditions to execute at specific intervals.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) Malicious programs allow adversaries control of all aspects of the process enabled by the PLC. Once the project file is downloaded to a PLC the workstation device may be disconnected with the infected project file still executing.(Citation: PLCdev) | https://attack.mitre.org/versions/v19/techniques/T0873/ | 1.1 | 2026-05-12T15:12:00.723Z
T0873.001 | Siemens Project File Format | T0873 | TA0110 | [field absent] | ICS | A0001 | Adversaries may infect Siemens PLC project files (i.e., Step 7, WinCC, etc.) to achieve Execution, Persistence, and Lateral Movement objectives. Adversaries may modify an existing project file or bring their own project files into the environment.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) The ability for an adversary to deploy an infected project file relies on access to a workstation with Siemens PLC programming software installed on it from which a program download can be performed. | https://attack.mitre.org/versions/v19/techniques/T0873/001/ | 1.0 | 2026-05-12T15:12:00.625Z
T0874 | Hooking |  | TA0104; TA0111 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0014; A0015; A0016; A0017; A0018 | Adversaries may hook into application programming interface (API) functions used by processes to redirect calls for execution and privilege escalation means. Windows processes often leverage these API functions to perform tasks that require reusable system resources. Windows API functions are typically stored in dynamic-link libraries (DLLs) as exported functions. (Citation: Enterprise ATT&CK) One type of hooking seen in ICS involves redirecting calls to these functions via import address table (IAT) hooking. IAT hooking uses modifications to a process IAT, where pointers to imported API functions are stored. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | https://attack.mitre.org/versions/v19/techniques/T0874/ | 1.2 | 2025-04-15T19:58:56.978Z
T0877 | I/O Image |  | TA0100 | None | ICS | A0003; A0010; A0017; A0018 | Adversaries may seek to capture process values related to the inputs and outputs of a PLC. During the scan cycle, a PLC reads the status of all inputs and stores them in an image table. (Citation: Nanjundaiah, Vaidyanath) The image table is the PLCs internal storage location where values of inputs/outputs for one scan are stored while it executes the user program. After the PLC has solved the entire logic program, it updates the output image table. The contents of this output image table are written to the corresponding output points in I/O Modules. The Input and Output Image tables described above make up the I/O Image on a PLC. This image is used by the user program instead of directly interacting with physical I/O. (Citation: Spenneberg, Ralf 2016) Adversaries may collect the I/O Image state of a PLC by utilizing a devices Native API to access the memory regions directly. The collection of the PLCs I/O state could be used to replace values or inform future stages of an attack. | https://attack.mitre.org/versions/v19/techniques/T0877/ | 1.1 | 2025-04-16T21:26:14.462Z
T0878 | Alarm Suppression |  | TA0107 | None | ICS | A0002; A0003; A0004; A0005; A0006; A0007; A0009; A0010; A0017; A0018 | Adversaries may target protection function alarms to prevent them from notifying operators of critical conditions. Alarm messages may be a part of an overall reporting system and of particular interest for adversaries. Disruption of the alarm system does not imply the disruption of the reporting system as a whole. A Secura presentation on targeting OT notes a dual fold goal for adversaries attempting alarm suppression: prevent outgoing alarms from being raised and prevent incoming alarms from being responded to. (Citation: Jos Wetzels, Marina Krotofil 2019) The method of suppression may greatly depend on the type of alarm in question: * An alarm raised by a protocol message * An alarm signaled with I/O * An alarm bit set in a flag (and read) In ICS environments, the adversary may have to suppress or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: Jos Wetzels, Marina Krotofil 2019) Methods of suppression may involve tampering or altering device displays and logs, modifying in memory code to fixed values, or even tampering with assembly level instruction code. | https://attack.mitre.org/versions/v19/techniques/T0878/ | 1.2 | 2025-04-16T21:26:11.789Z
T0879 | Damage to Property |  | TA0105 | None | ICS |  | Adversaries may cause damage and destruction of property to infrastructure, equipment, and the surrounding environment when attacking control systems. This technique may result in device and operational equipment breakdown, or represent tangential damage from other techniques used in an attack. Depending on the severity of physical damage and disruption caused to control processes and systems, this technique may result in Loss of Safety. Operations that result in Loss of Control may also cause damage to property, which may be directly or indirectly motivated by an adversary seeking to cause impact in the form of Loss of Productivity and Revenue. The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill under an incidents affecting business section of its 2014 IT Security Report. (Citation: BSI State of IT Security 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact and damage resulted from the uncontrolled shutdown of a blast furnace. A Polish student used a remote controller device to interface with the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) (Citation: Bruce Schneier January 2008) Using this remote, the student was able to capture and replay legitimate tram signals. This resulted in damage to impacted trams, people, and the surrounding property. Reportedly, four trams were derailed and were forced to make emergency stops. (Citation: Shelley Smith February 2008) Commands issued by the student may have also resulted in tram collisions, causing harm to those on board and the environment outside. (Citation: Bruce Schneier January 2008) | https://attack.mitre.org/versions/v19/techniques/T0879/ | 1.1 | 2025-04-16T21:26:15.731Z
T0880 | Loss of Safety |  | TA0105 | None | ICS |  | Adversaries may compromise safety system functions designed to maintain safe operation of a process when unacceptable or dangerous conditions occur. Safety systems are often composed of the same elements as control systems but have the sole purpose of ensuring the process fails in a predetermined safe manner. Many unsafe conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable safety system functions as a prerequisite to subsequent attack execution or to allow for future unsafe conditionals to go unchecked. Detection of a Loss of Safety by operators can result in the shutdown of a process due to strict policies regarding safety systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. | https://attack.mitre.org/versions/v19/techniques/T0880/ | 1.0 | 2025-04-16T21:26:14.990Z
T0881 | Service Stop |  | TA0107 | None | ICS | A0001; A0002; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0015; A0016 | Adversaries may stop or disable services on a system to render those services unavailable to legitimate users. Stopping critical services can inhibit or stop response to an incident or aid in the adversary's overall objectives to cause damage to the environment. (Citation: Enterprise ATT&CK) Services may not allow for modification of their data stores while running. Adversaries may stop services in order to conduct Data Destruction. (Citation: Enterprise ATT&CK) | https://attack.mitre.org/versions/v19/techniques/T0881/ | 1.1 | 2025-04-15T19:58:03.170Z
T0882 | Theft of Operational Information |  | TA0105 | None | ICS |  | Adversaries may steal operational information on a production environment as a direct mission outcome for personal gain or to inform future operations. This information may include design documents, schedules, rotational data, or similar artifacts that provide insight on operations. In the Bowman Dam incident, adversaries probed systems for operational data. (Citation: Mark Thompson March 2016) (Citation: Danny Yadron December 2015) | https://attack.mitre.org/versions/v19/techniques/T0882/ | 1.0 | 2026-05-12T15:12:00.709Z
T0883 | Internet Accessible Device |  | TA0108 | None | ICS | A0001; A0008; A0011; A0015; A0016 | Adversaries may gain access into industrial environments through systems exposed directly to the internet for remote access rather than through External Remote Services. Internet Accessible Devices are exposed to the internet unintentionally or intentionally without adequate protections. This may allow for adversaries to move directly into the control system network. Access onto these devices is accomplished without the use of exploits, these would be represented within the Exploit Public-Facing Application technique. Adversaries may leverage built in functions for remote access which may not be protected or utilize minimal legacy protections that may be targeted. (Citation: NCCIC January 2014) These services may be discoverable through the use of online scanning tools. In the case of the Bowman dam incident, adversaries leveraged access to the dam control network through a cellular modem. Access to the device was protected by password authentication, although the application was vulnerable to brute forcing. (Citation: NCCIC January 2014) (Citation: Danny Yadron December 2015) (Citation: Mark Thompson March 2016) In Trend Micros manufacturing deception operations adversaries were detected leveraging direct internet access to an ICS environment through the exposure of operational protocols such as Siemens S7, Omron FINS, and EtherNet/IP, in addition to misconfigured VNC access. (Citation: Stephen Hilt, Federico Maggi, Charles Perine, Lord Remorin, Martin Rsler, and Rainer Vosseler) | https://attack.mitre.org/versions/v19/techniques/T0883/ | 1.0 | 2025-04-16T21:26:20.494Z
T0884 | Connection Proxy |  | TA0101 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Adversaries may use a connection proxy to direct network traffic between systems or act as an intermediary for network communications. The definition of a proxy can also be expanded to encompass trust relationships between networks in peer-to-peer, mesh, or trusted connections between networks consisting of hosts or systems that regularly communicate with each other. The network may be within a single organization or across multiple organizations with trust relationships. Adversaries could use these types of relationships to manage command and control communications, to reduce the number of simultaneous outbound network connections, to provide resiliency in the face of connection loss, or to ride over existing trusted communications paths between victims to avoid suspicion. (Citation: Enterprise ATT&CK January 2018) | https://attack.mitre.org/versions/v19/techniques/T0884/ | 1.1 | 2025-04-16T21:26:19.127Z
T0885 | Commonly Used Port |  | TA0101 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Adversaries may communicate over a commonly used port to bypass firewalls or network detection systems and to blend in with normal network activity, to avoid more detailed inspection. They may use the protocol associated with the port, or a completely different protocol. They may use commonly open ports, such as the examples provided below. * TCP:80 (HTTP) * TCP:443 (HTTPS) * TCP/UDP:53 (DNS) * TCP:1024-4999 (OPC on XP/Win2k3) * TCP:49152-65535 (OPC on Vista and later) * TCP:23 (TELNET) * UDP:161 (SNMP) * TCP:502 (MODBUS) * TCP:102 (S7comm/ISO-TSAP) * TCP:20000 (DNP3) * TCP:44818 (Ethernet/IP) | https://attack.mitre.org/versions/v19/techniques/T0885/ | 1.1 | 2026-05-12T15:12:00.723Z
T0886 | Remote Services |  | TA0108; TA0109 | None | ICS | A0002; A0006; A0007; A0008; A0009; A0011; A0012; A0015; A0017 | Adversaries may leverage remote services to move between assets and network segments. These services are often used to allow operators to interact with systems remotely within the network, some examples are RDP, SMB, SSH, and other similar mechanisms. (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) (Citation: Dragos December 2017) (Citation: Joe Slowik April 2019) Remote services could be used to support remote access, data transmission, authentication, name resolution, and other remote functions. Further, remote services may be necessary to allow operators and administrators to configure systems within the network from their engineering or management workstations. An adversary may use this technique to access devices which may be dual-homed (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) to multiple network segments, and can be used for Program Download or to execute attacks on control devices directly through Valid Accounts. Specific remote services (RDP & VNC) may be a precursor to enable Graphical User Interface execution on devices such as HMIs or engineering workstation software. Based on incident data, CISA and FBI assessed that Chinese state-sponsored actors also compromised various authorized remote access channels, including systems designed to transfer data and/or allow access between corporate and ICS networks. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/versions/v19/techniques/T0886/ | 1.1 | 2026-05-12T15:12:00.722Z
T0887 | Wireless Sniffing |  | TA0102; TA0100 | None | ICS | A0001; A0013 | Adversaries may seek to capture radio frequency (RF) communication used for remote control and reporting in distributed environments. RF communication frequencies vary between 3 kHz to 300 GHz, although are commonly between 300 MHz to 6 GHz. (Citation: Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K. April 2018) The wavelength and frequency of the signal affect how the signal propagates through open air, obstacles (e.g. walls and trees) and the type of radio required to capture them. These characteristics are often standardized in the protocol and hardware and may have an effect on how the signal is captured. Some examples of wireless protocols that may be found in cyber-physical environments are: WirelessHART, Zigbee, WIA-FA, and 700 MHz Public Safety Spectrum. Adversaries may capture RF communications by using specialized hardware, such as software defined radio (SDR), handheld radio, or a computer with radio demodulator tuned to the communication frequency. (Citation: Bastille April 2017) Information transmitted over a wireless medium may be captured in-transit whether the sniffing device is the intended destination or not. This technique may be particularly useful to an adversary when the communications are not encrypted. (Citation: Gallagher, S. April 2017) In the 2017 Dallas Siren incident, it is suspected that adversaries likely captured wireless command message broadcasts on a 700 MHz frequency during a regular test of the system. These messages were later replayed to trigger the alarm systems. (Citation: Gallagher, S. April 2017) | https://attack.mitre.org/versions/v19/techniques/T0887/ | 1.1 | 2025-04-16T21:26:10.392Z
T0888 | Remote System Information Discovery |  | TA0102 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0015; A0016; A0017; A0018 | An adversary may attempt to get detailed information about remote systems and their peripherals, such as make/model, role, and configuration. Adversaries may use information from Remote System Information Discovery to aid in targeting and shaping follow-on behaviors. For example, the system's operational role and model information can dictate whether it is a relevant target for the adversary's operational objectives. In addition, the system's configuration may be used to scope subsequent technique usage. Requests for system information are typically implemented using automation and management protocols and are often automatically requested by vendor software during normal operation. This information may be used to tailor management actions, such as program download and system or module firmware. An adversary may leverage this same information by issuing calls directly to the system's API. | https://attack.mitre.org/versions/v19/techniques/T0888/ | 1.1 | 2026-05-12T15:12:00.624Z
T0889 | Modify Program |  | TA0110 | None | ICS | A0003; A0010; A0017; A0018 | Adversaries may modify or add a program on a controller to affect how it interacts with the physical process, peripheral devices and other hosts on the network. Modification to controller programs can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Program modification encompasses the addition and modification of instructions and logic contained in Program Organization Units (POU) (Citation: IEC February 2013) and similar programming elements found on controllers. This can include, for example, adding new functions to a controller, modifying the logic in existing functions and making new calls from one function to another. Some programs may allow an adversary to interact directly with the native API of the controller to take advantage of obscure features or vulnerabilities. | https://attack.mitre.org/versions/v19/techniques/T0889/ | 1.2 | 2025-04-15T19:59:24.213Z
T0890 | Exploitation for Privilege Escalation |  | TA0111 | None | ICS | A0001; A0002; A0003; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0014; A0015; A0016; A0017; A0018 | Adversaries may exploit software vulnerabilities in an attempt to elevate privileges. Exploitation of a software vulnerability occurs when an adversary takes advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Security constructs such as permission levels will often hinder access to information and use of certain techniques, so adversaries will likely need to perform privilege escalation to include use of software exploitation to circumvent those restrictions. (Citation: The MITRE Corporation) When initially gaining access to a system, an adversary may be operating within a lower privileged process which will prevent them from accessing certain resources on the system. Vulnerabilities may exist, usually in operating system components and software commonly running at higher permissions, that can be exploited to gain higher levels of access on the system. This could enable someone to move from unprivileged or user level permissions to SYSTEM or root permissions depending on the component that is vulnerable. This may be a necessary step for an adversary compromising an endpoint system that has been properly configured and limits other privilege escalation methods. (Citation: The MITRE Corporation) | https://attack.mitre.org/versions/v19/techniques/T0890/ | 1.1 | 2025-04-16T21:26:18.792Z
T0892 | Change Credential |  | TA0107 | None | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0014; A0015; A0016; A0017; A0018 | Adversaries may modify software and device credentials to prevent operator and responder access. Depending on the device, the modification or addition of this password could prevent any device configuration actions from being accomplished and may require a factory reset or replacement of hardware. These credentials are often built-in features provided by the device vendors as a means to restrict access to management interfaces. An adversary with access to valid or hardcoded credentials could change the credential to prevent future authorized device access. Change Credential may be especially damaging when paired with other techniques such as Modify Program, Data Destruction, or Modify Controller Tasking. In these cases, a device’s configuration may be destroyed or include malicious actions for the process environment, which cannot not be removed through normal device configuration actions. Additionally, recovery of the device and original configuration may be difficult depending on the features provided by the device. In some cases, these passwords cannot be removed onsite and may require that the device be sent back to the vendor for additional recovery steps. A chain of incidents occurred in Germany, where adversaries locked operators out of their building automation system (BAS) controllers by enabling a previously unset BCU key. (Citation: German BAS Lockout Dec 2021) | https://attack.mitre.org/versions/v19/techniques/T0892/ | 1.0 | 2026-05-12T15:12:00.726Z
T0893 | Data from Local System |  | TA0100 | None | ICS | A0001; A0002; A0006; A0007; A0008; A0012; A0015; A0016 | Adversaries may target and collect data from local system sources, such as file systems, configuration files, or local databases. This can include sensitive data such as specifications, schematics, or diagrams of control system layouts, devices, and processes. Adversaries may do this using Command-Line Interface or Scripting techniques to interact with the file system to gather information. Adversaries may also use Automated Collection on the local system. | https://attack.mitre.org/versions/v19/techniques/T0893/ | 1.0 | 2025-04-15T19:59:23.577Z
T0894 | System Binary Proxy Execution |  | TA0103 | None | ICS | A0001; A0002; A0006; A0007; A0008; A0012 | Adversaries may bypass process and/or signature-based defenses by proxying execution of malicious content with signed, or otherwise trusted, binaries. Binaries used in this technique are often Microsoft-signed files, indicating that they have been either downloaded from Microsoft or are already native in the operating system. (Citation: LOLBAS Project) Binaries signed with trusted digital certificates can typically execute on Windows systems protected by digital signature validation. Several Microsoft signed binaries that are default on Windows installations can be used to proxy execution of other files or commands. Similarly, on Linux systems adversaries may abuse trusted binaries such as split to proxy execution of malicious commands. (Citation: split man page)(Citation: GTFO split) Adversaries may abuse application binaries installed on a system for proxy execution of malicious code or domain-specific commands. These commands could be used to target local resources on the device or networked devices within the environment through defined APIs (Execution through API) or application-specific programming languages (e.g., MicroSCADA SCIL). Application binaries may be signed by the developer or generally trusted by the operators, analysts, and monitoring tools accustomed to the environment. These applications may be developed and/or directly provided by the device vendor to enable configuration, management, and operation of their devices without many alternatives. Adversaries may seek to target these trusted application binaries to execute or send commands without the development of custom malware. For example, adversaries may target a SCADA server binary which has the existing ability to send commands to substation devices, such as through IEC 104 command messages. Proxy execution may still require the development of custom tools to hook into the application binary’s execution. | https://attack.mitre.org/versions/v19/techniques/T0894/ | 1.0 | 2025-04-15T19:58:11.559Z
T0895 | Autorun Image |  | TA0104 | [field absent] | ICS | A0001; A0002; A0006; A0007; A0008; A0012 | Adversaries may leverage AutoRun functionality or scripts to execute malicious code. Devices configured to enable AutoRun functionality or legacy operating systems may be susceptible to abuse of these features to run malicious code stored on various forms of removeable media (i.e., USB, Disk Images [.ISO]). Commonly, AutoRun or AutoPlay are disabled in many operating systems configurations to mitigate against this technique. If a device is configured to enable AutoRun or AutoPlay, adversaries may execute code on the device by mounting the removable media to the device, either through physical or virtual means. This may be especially relevant for virtual machine environments where disk images may be dynamically mapped to a guest system on a hypervisor. An example could include an adversary gaining access to a hypervisor through the management interface to modify a virtual machine’s hardware configuration. They could then deploy an iso image with a malicious AutoRun script to cause the virtual machine to automatically execute the code contained on the disk image. This would enable the execution of malicious code within a virtual machine without needing any prior remote access to that system. | https://attack.mitre.org/versions/v19/techniques/T0895/ | 1.0 | 2025-04-15T19:58:42.824Z
T1691 | Block Operational Technology Message |  | TA0107 | [field absent] | ICS | A0002; A0003; A0004; A0005; A0007; A0010; A0013; A0017; A0018 | Adversaries may block messages between systems and devices in an OT/ICS environment to disrupt processes. Messages typically fall into two categories: (1) reporting messages that contain telemetry data about the current state of systems, devices, and processes and (2) command messages that contain instructions to control systems, devices, and processes. Both types of messages are critical for the proper functioning of industrial control processes and failure of the messages to reach their intended destinations could inhibit response functions or create an unsafe condition that could have physical impacts.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011)(Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) Adversaries may block communications by either making modifications to software (System Firmware, Module Firmware, Hooking, and Rootkit) and services (Service Stop, Denial of Service) on systems and devices or by positioning themselves between systems and devices and intercepting and blocking the communications such as the case with an Adversary-in-the-Middle attack. | https://attack.mitre.org/versions/v19/techniques/T1691/ | 1.0 | 2026-05-12T15:12:00.624Z
T1691.001 | Command Message | T1691 | TA0107 | [field absent] | ICS | A0002; A0003; A0004; A0005; A0007; A0010; A0013; A0017; A0018 | Adversaries may block a command message from reaching its intended target to prevent command execution. In OT networks, command messages are sent to provide instructions to control system devices. A blocked command message can inhibit response functions from correcting a disruption or unsafe condition.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011)(Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) | https://attack.mitre.org/versions/v19/techniques/T1691/001/ | 1.0 | 2026-05-12T15:12:00.621Z
T1691.002 | Reporting Message | T1691 | TA0107 | [field absent] | ICS | A0002; A0003; A0004; A0005; A0007; A0009; A0010; A0013; A0017; A0018 | Adversaries may block or prevent a reporting message from reaching its intended target. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. By blocking these reporting messages, an adversary can potentially hide their actions from an operator. Blocking reporting messages in control systems that manage physical processes may contribute to system impact, causing inhibition of a response function. A control system may not be able to respond in a proper or timely manner to an event, such as a dangerous fault, if its corresponding reporting message is blocked.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011)(Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) | https://attack.mitre.org/versions/v19/techniques/T1691/002/ | 1.0 | 2026-05-12T15:12:00.643Z
T1692 | Unauthorized Message |  | TA0103; TA0106 | [field absent] | ICS | A0002; A0003; A0004; A0005; A0007; A0010; A0017; A0018 | Adversaries may send unauthorized messages to ICS systems and devices to evade defenses or manipulate processes. Unauthorized messages can be categorized as either reporting messages that contain telemetry data about the current state of systems, devices, and processes or as command messages which instruct systems and devices on how to operate. By injecting unauthorized messages, adversaries can make it appear as if everything is working correctly when it isn’t, trigger alarms to misdirect personnel or impact processes, and manipulate controls to disrupt processes.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) Adversaries may send unauthorized messages in an ICS environment using software found within the environment (living-off-the-land, vendor-specific interfaces, etc.), custom tooling leveraging OT protocols and libraries, or by positioning themselves between systems and devices and injecting messages into the communications such as the case with an Adversary-in-the-Middle attack. | https://attack.mitre.org/versions/v19/techniques/T1692/ | 1.0 | 2026-05-12T15:12:00.722Z
T1692.001 | Command Message | T1692 | TA0103; TA0106 | [field absent] | ICS | A0002; A0003; A0004; A0005; A0007; A0010; A0017; A0018 | Adversaries may send unauthorized command messages to instruct control system assets to perform actions outside of their intended functionality, or without the logical preconditions to trigger their expected function. Command messages are used in ICS networks to give direct instructions to control systems devices. If an adversary can send an unauthorized command message to a control system, then it can instruct the control systems device to perform an action outside the normal bounds of the device's actions. An adversary could potentially instruct a control systems device to perform an action that will cause an Impact.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) In the Dallas Siren incident, adversaries were able to send command messages to activate tornado alarm systems across the city without an impending tornado or other disaster.(Citation: Zack Whittaker April 2017)(Citation: Benjamin Freed March 2019) | https://attack.mitre.org/versions/v19/techniques/T1692/001/ | 1.0 | 2026-05-12T15:12:00.629Z
T1692.002 | Reporting Message | T1692 | TA0103; TA0106 | [field absent] | ICS | A0002; A0003; A0004; A0005; A0007; A0009; A0010; A0017; A0018 | Adversaries may spoof reporting messages in control system environments for evasion and to impair process control. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. Reporting messages are important for monitoring the normal operation of a system or identifying important events such as deviations from expected values. If an adversary has the ability to Spoof Reporting Messages, they can impact the control system in many ways. The adversary can Spoof Reporting Messages that state that the process is operating normally, as a form of evasion. The adversary could also Spoof Reporting Messages to make the defenders and operators think that other errors are occurring in order to distract them from the actual source of a problem.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) | https://attack.mitre.org/versions/v19/techniques/T1692/002/ | 1.0 | 2026-05-12T15:12:00.633Z
T1693 | Modify Firmware |  | TA0110; TA0107; TA0106 | [field absent] | ICS | A0003; A0010; A0017; A0018 | Firmware is low-level software embedded in hardware that enables systems and devices to function properly and is commonly found in ICS environments. Adversaries may modify firmware on a system or device by installing malicious or vulnerable versions that enable them to achieve objectives such as Persistence, Impair Process Control, and Inhibit Response Function. Adversaries may modify system and device firmware by using the built-in firmware update functionality which may support local or remote installation. The malicious or vulnerable firmware may be delivered via Replication Through Removable Media, Supply Chain Compromise, or Remote Services. Once installed, the malicious or vulnerable firmware could be used to provide Rootkit and Hooking functionality, Exploitation for Privilege Escalation, or Denial of Service.(Citation: Basnight, Zachry, et al.) | https://attack.mitre.org/versions/v19/techniques/T1693/ | 1.0 | 2026-05-12T15:12:00.643Z
T1693.001 | System Firmware | T1693 | TA0110; TA0107; TA0106 | [field absent] | ICS | A0002; A0003; A0004; A0005; A0009; A0010; A0011; A0015; A0016; A0017 | System firmware on modern assets is often designed with an update feature. Older device firmware may be factory installed and require special reprograming equipment. When available, the firmware update feature enables vendors to remotely patch bugs and perform upgrades. Device firmware updates are often delegated to the user and may be done using a software update package. It may also be possible to perform this task over the network. An adversary may exploit the firmware update feature on accessible devices to upload malicious or out-of-date firmware. Malicious modification of device firmware may provide an adversary with root access to a device, given firmware is one of the lowest programming abstraction layers.(Citation: Basnight, Zachry, et al.) | https://attack.mitre.org/versions/v19/techniques/T1693/001/ | 1.0 | 2026-05-12T15:12:00.639Z
T1693.002 | Module Firmware | T1693 | TA0110; TA0107; TA0106 | [field absent] | ICS | A0003; A0010; A0017; A0018 | Adversaries may install malicious or vulnerable firmware onto modular hardware devices. Control system devices often contain modular hardware devices. These devices may have their own set of firmware that is separate from the firmware of the main control system equipment. This technique is similar to System Firmware, but is conducted on other system components that may not have the same capabilities or level of integrity checking. Although it results in a device re-image, malicious device firmware may provide persistent access to remaining devices.(Citation: Daniel Peck, Dale Peterson January 2009) An easy point of access for an adversary is the Ethernet card, which may have its own CPU, RAM, and operating system. The adversary may attack and likely exploit the computer on an Ethernet card. Exploitation of the Ethernet card computer may enable the adversary to accomplish additional attacks, such as the following:(Citation: Daniel Peck, Dale Peterson January 2009) * Delayed Attack - The adversary may stage an attack in advance and choose when to launch it, such as at a particularly damaging time. * Brick the Ethernet Card - Malicious firmware may be programmed to result in an Ethernet card failure, requiring a factory return. * Random Attack or Failure - The adversary may load malicious firmware onto multiple field devices. Execution of an attack and the time it occurs is generated by a pseudo-random number generator. * A Field Device Worm - The adversary may choose to identify all field devices of the same model, with the end goal of performing a device-wide compromise. * Attack Other Cards on the Field Device - Although it is not the most important module in a field device, the Ethernet card is most accessible to the adversary and malware. Compromise of the Ethernet card may provide a more direct route to compromising other modules, such as the CPU module. | https://attack.mitre.org/versions/v19/techniques/T1693/002/ | 1.0 | 2026-05-12T15:12:00.642Z
T1694 | Insecure Credentials |  | TA0110; TA0109 | [field absent] | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Adversaries may target insecure credentials as a means to persist on a system or device or move laterally from one system or device to another. Insecure credentials may appear as default credentials which are pre-configured credentials on a system, device, or software that are well-known in documentation or hard-coded credentials which are built into the system, device, or software that cannot be changed or not easily changed because of the impact on control processes.(Citation: NIST SP 800-82r3)(Citation: ICS-ALERT-13-164-01)(Citation: OT IceFall) Adversaries often times use insecure credentials to evade detection as they are typically forgotten about by system and device owners. | https://attack.mitre.org/versions/v19/techniques/T1694/ | 1.0 | 2026-05-12T15:12:00.628Z
T1694.001 | Default Credentials | T1694 | TA0110; TA0109 | [field absent] | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Adversaries may leverage manufacturer or supplier set default credentials on control system devices. These default credentials may have administrative permissions and may be necessary for initial configuration of the device. It is general best practice to change the passwords for these accounts as soon as possible, but some manufacturers may have devices that have passwords or usernames that cannot be changed.(Citation: Keith Stouffer May 2015) Default credentials are normally documented in an instruction manual that is either packaged with the device, published online through official means, or published online through unofficial means. Adversaries may leverage default credentials that have not been properly modified or disabled. | https://attack.mitre.org/versions/v19/techniques/T1694/001/ | 1.0 | 2026-05-12T15:12:00.634Z
T1694.002 | Hardcoded Credentials | T1694 | TA0110; TA0109 | [field absent] | ICS | A0013 | Adversaries may leverage credentials that are hardcoded in software or firmware to gain an unauthorized interactive user session to an asset. Examples credentials that may be hardcoded in an asset include: * Username/Passwords * Cryptographic keys/Certificates * API tokens Unlike Default Credentials, these credentials are built into the system in a way that they either cannot be changed by the asset owner, or may be infeasible to change because of the impact it would cause to the control system operation. These credentials may be reused across whole product lines or device models and are often not published or known to the owner and operators of the asset.(Citation: ICS-ALERT-13-164-01)(Citation: OT IceFall) Adversaries may utilize these hardcoded credentials to move throughout the control system environment or provide reliable access for their tools to interact with industrial assets. | https://attack.mitre.org/versions/v19/techniques/T1694/002/ | 1.0 | 2026-05-12T15:12:00.640Z
T1695 | Block Communications |  | TA0107 | [field absent] | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Operational technology communications occur over serial COM, Ethernet, Wi-Fi, cellular (4G/5G), and satellite mediums. Adversaries may block communications to prevent reporting messages and command messages from reaching their intended target devices disrupting processes, operations, and causing cyber-physical impacts.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) Adversaries may block communications by either making modifications to software (System Firmware, Module Firmware, Hooking, and Rootkit) and services (Service Stop, Denial of Service) on systems and devices or by positioning themselves between systems and devices and intercepting and blocking the communications such as the case with an Adversary-in-the-Middle attack. | https://attack.mitre.org/versions/v19/techniques/T1695/ | 1.0 | 2026-05-12T15:12:00.726Z
T1695.001 | Serial COM | T1695 | TA0107 | [field absent] | ICS | A0001; A0002; A0003; A0004; A0005; A0007; A0009; A0010; A0011; A0012; A0013; A0017; A0018 | Adversaries may block access to serial COM to prevent instructions or configurations from reaching target devices. Serial Communication ports (COM) allow communication with control system devices. Devices can receive command and configuration messages over such serial COM. Devices also use serial COM to send command and reporting messages. Blocking device serial COM may also block command messages and block reporting messages. A serial to Ethernet converter is often connected to a serial COM to facilitate communication between serial and Ethernet devices. One approach to blocking a serial COM would be to create and hold open a TCP session with the Ethernet side of the converter. A serial to Ethernet converter may have a few ports open to facilitate multiple communications. For example, if there are three serial COM available -- 1, 2 and 3 --, the converter might be listening on the corresponding ports 20001, 20002, and 20003. If a TCP/IP connection is opened with one of these ports and held open, then the port will be unavailable for use by another party. One way the adversary could achieve this would be to initiate a TCP session with the serial to Ethernet converter at 10.0.0.1 via Telnet on serial port 1 with the following command: telnet 10.0.0.1 20001. | https://attack.mitre.org/versions/v19/techniques/T1695/001/ | 1.0 | 2026-05-12T15:12:00.634Z
T1695.002 | Ethernet | T1695 | TA0107 | [field absent] | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Adversaries may block access to Ethernet communications to prevent instructions or configurations messages from reaching target systems and devices. Ethernet connections allow for communications between IT and OT systems and devices. Blocking Ethernet communications may also block command and reporting messages.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) An adversary may block Ethernet communications by disabling network interfaces, Service Stop, or conducting an Adversary-in-the-Middle attack and dropping the network traffic. | https://attack.mitre.org/versions/v19/techniques/T1695/002/ | 1.0 | 2026-05-12T15:12:00.635Z
T1695.003 | Wi-Fi | T1695 | TA0107 | [field absent] | ICS | A0001; A0002; A0003; A0004; A0005; A0006; A0007; A0008; A0009; A0010; A0011; A0012; A0013; A0014; A0015; A0016; A0017; A0018 | Adversaries may block access to Wi-Fi communications to prevent messages from reaching target systems and devices. Wi-Fi connections allow for communications between IT and OT systems and devices. Blocking Wi-Fi communications may also block command and reporting messages.(Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) An adversary may block Wi-Fi communications by disabling network interfaces, Service Stop, conducting an Adversary-in-the-Middle attack and dropping the network traffic, or by jamming the Wi-Fi signal. | https://attack.mitre.org/versions/v19/techniques/T1695/003/ | 1.0 | 2026-05-12T15:12:00.641Z

## Asset Catalog
ID | Role | Raw platforms | Description | MITRE page
A0001 | Workstation | Linux; Windows | Workstations are devices used by human operators or engineers to perform various configuration, programming, maintenance, diagnostic, or operational tasks. Workstations typically utilize standard desktop or laptop hardware and operating systems (e.g., MS Windows), but run dedicated control system applications or diagnostic/management software to support interfacing with the control servers or field devices. Some workstations have a fixed location within the network architecture, while others are transient devices that are directly connected to various field devices to support local management activities. | https://attack.mitre.org/versions/v19/assets/A0001/
A0002 | Human-Machine Interface (HMI) | Linux; Windows | Human-Machine Interfaces (HMIs) are systems used by an operator to monitor the real-time status of an operational process and to perform necessary control functions, including the adjustment of device parameters. An HMI can take various forms, including a dedicated screen or control panel integrated with a specific device/controller, or a customizable software GUI application running on a standard operating system (e.g., MS Windows) that interfaces with a control/SCADA server. The HMI is critical to ensuring operators have sufficient visibility and control over the operational process. | https://attack.mitre.org/versions/v19/assets/A0002/
A0003 | Programmable Logic Controller (PLC) | Embedded | A Programmable Logic Controller (PLC) is an embedded programmable control device. PLCs typically utilize a modular architecture with separate modules used to support its processing capabilities, communication mediums, and I/O interfaces. PLCs allow for the deployment of customized programs/logic to control or monitor an operational process. This logic is defined using industry specific programming languages, such as IEC 61131 (Citation: IEC February 2013), which define the set of tasks and program organizational units (POUs) included in the device’s programs. PLCs also typically have distinct operating modes (e.g., Remote, Run, Program, Stop) which are used to determine when the device can be programmed or whether it should execute the custom logic. | https://attack.mitre.org/versions/v19/assets/A0003/
A0004 | Remote Terminal Unit (RTU) | Embedded; Linux; Windows | A Remote Terminal Unit (RTU) is a device that typically resides between field devices (e.g., PLCs, IEDs) and control/SCADA servers and supports various communication interfacing and data aggregation functions. RTUs are typically responsible for forwarding commands from the control server and the collection of telemetry, events, and alerts from the field devices. An RTU can be implemented as a dedicated embedded device, as software platform that runs on a hardened/ruggedized computer, or using a custom application program on a PLC. | https://attack.mitre.org/versions/v19/assets/A0004/
A0005 | Intelligent Electronic Device (IED) | Embedded | An Intelligent Electronic Device (IED) is a type of specialized field device that is designed to perform specific operational functions, frequently for protection, monitoring, or control within the electric sector. IEDs are typically used to both acquire telemetry and execute tailored control algorithms/actions based on customizable parameters/settings. An IED is usually implemented as a dedicated embedded device and supports various network automation protocols to communicate with RTUs and Control Servers. | https://attack.mitre.org/versions/v19/assets/A0005/
A0006 | Data Historian | Embedded; Linux; Windows | Data historians, or historian, are systems used to collect and store data, including telemetry, events, alerts, and alarms about the operational process and supporting devices. The historian typically utilizes a database to store this data, and commonly provide tools and interfaces to support the analysis of the data. Data historians are often used to support various engineering or business analysis functions and therefore commonly needs access from the corporate network. Data historians often work in a hierarchical paradigm where lower/site level historians collect and store data which is then aggregated into a site/plant level historian. Therefore, data historians often have remote services that can be accessed externally from the ICS network. Many data historian vendors have designed their software to securely transfer data between the ICS and business networks instead of requiring business systems to access the data historian in the ICS network directly. | https://attack.mitre.org/versions/v19/assets/A0006/
A0007 | Control Server | Embedded; Linux; Windows | Control servers are typically a software platform that runs on a modern server operating system (e.g., MS Windows Server). The server typically uses one or more automation protocols (e.g., Modbus, DNP3) to communicate with the various low-level control devices such as Remote Terminal Units (RTUs) and Programmable Logic Controllers (PLCs). The control server also usually provides an interface/network service to connect with an HMI. | https://attack.mitre.org/versions/v19/assets/A0007/
A0008 | Application Server | Linux; Windows | Application servers are used across many different sectors to host various diverse software applications necessary to supporting the ICS. Example functions can include data analytics and reporting, alarm management, and the management/coordination of different control servers. The application server typically runs on a modern server operating system (e.g., MS Windows Server). | https://attack.mitre.org/versions/v19/assets/A0008/
A0009 | Data Gateway | Windows; Linux; Embedded; Network | Data Gateway is a device that supports the communication and exchange of data between different systems, networks, or protocols within the ICS. Different types of data gateways are used to perform various functions, including: * Protocol Translation: Enable communication to devices that support different or incompatible protocols by translating information from one protocol to another. * Media Converter: Convert data across different Layer 1 and 2 network protocols / mediums, for example, converting from Serial to Ethernet. * Data Aggregation: Collect and combine data from different devices into one consistent format and protocol interface. * Data Mirroring: Create a real-time, exact copy of data streams from devices to a separate destination for redundancy, monitoring, or backup purposes. Data gateways are often critical to the forwarding/transmission of critical control or monitoring data within the ICS. Further, these devices often have remote various network services that are used to communicate across different zones or networks. These assets may focus on a single function listed below or combinations of these functions to best fit the industry use-case. | https://attack.mitre.org/versions/v19/assets/A0009/
A0010 | Safety Controller | Embedded | Safety controllers are typically a type of field device used to perform the safety critical function. Safety controllers often support the deployment of custom programs/logic, similar to a PLC, but can also be tailored for sector specific functions/applications. The safety controllers typically utilize redundant hardware and processors to ensure they operate reliably if a component fails. | https://attack.mitre.org/versions/v19/assets/A0010/
A0011 | Virtual Private Network (VPN) Server | Embedded; Linux; Windows | A VPN server is a device that is used to establish a secure network tunnel between itself and other remote VPN devices, including field VPNs. VPN servers can be used to establish a secure connection with a single remote device, or to securely bridge all traffic between two separate networks together by encapsulating all data between those networks. VPN servers typically support remote network services that are used by field VPNs to initiate the establishment of the secure VPN tunnel between the field device and server. | https://attack.mitre.org/versions/v19/assets/A0011/
A0012 | Jump Host | Embedded; Linux; Windows | Jump hosts are devices used to support remote management sessions into ICS networks or devices. The system is used to access the ICS environment securely from external networks, such as the corporate network. The user must first remote into the jump host before they can access ICS devices. The jump host may be a customized Windows server using common remote access protocols (e.g., RDP) or a dedicated access management device. The jump host typically performs various security functions to ensure the authenticity of remote sessions, including authentication, enforcing access controls/permissions, and auditing all access attempts. | https://attack.mitre.org/versions/v19/assets/A0012/
A0013 | Field I/O | Embedded | Field I/O are devices that communicate with a controller or data aggregator to either send input data or receive output data. Input data may include readings about a given environment/device state from sensors, while output data may include data sent back to actuators for them to either undertake actions or change parameter values.(Citation: Guidance - NIST SP800-82) These devices are frequently embedded devices running on lightweight embedded operating systems or RTOSes. | https://attack.mitre.org/versions/v19/assets/A0013/
A0014 | Routers | Embedded; Network | A computer that is a gateway between two networks at OSI layer 3 and that relays and directs data packets through that inter-network. The most common form of router operates on IP packets.(Citation: IETF RFC4949 2007) | https://attack.mitre.org/versions/v19/assets/A0014/
A0015 | Switch | Embedded; Network | A switch is a network device that connects endpoints (e.g., workstations, servers, HMIs, PLCs, etc.) so that they can communicate and share data and resources. Switches may operate at either Layer 2 or Layer 3 of the OSI Model and intelligently forward packets across the network based on the specified address (Media Access Control (MAC) address for Layer 2 and Internet Protocol (IP) address for Layer 3). Switches are typically used to define network segments and connect the devices within a particular level of the Purdue Model. | https://attack.mitre.org/versions/v19/assets/A0015/
A0016 | Firewall | Embedded; Windows; Linux; Network | A gateway that limits access between networks in accordance with local security policy. In ICS networks, firewalls can exist in multiple locations in the network architecture and serve a variety of purposes. The first, and often the most important, is the firewall segmenting the ICS network from the business network. This firewall acts as the primary network boundary point that controls the ingress/egress of network traffic between the ICS and business networks. This firewall may also be a single device connected to multiple network segments, where the firewall defines individual zones for the different network segments and can control access to the zones and between the zones. This can limit the ability of an adversary to traverse a network. | https://attack.mitre.org/versions/v19/assets/A0016/
A0017 | Distributed Control System (DCS) Controller | Embedded | A Distributed Control System (DCS) Controller is a microprocessor unit that is used to manage automation processes. DCS Controllers are often found in plants (chemical, manufacturing, oil and gas, etc.) where large scale continuous automation processes are required. A DCS Controller typically operates as part of a larger networked system with other DCS Controllers where each DCS Controller manages an individual part of a continuous process. In addition to these other controllers, DCS Controllers operate along side multiple other system components including system software, operator stations, and other embedded field controllers. The distributed nature of DCS Controllers provides scalability, redundancy, and improved process reliability. DCS Controllers are programmed using traditional process automation programming languages (IEC-61131). | https://attack.mitre.org/versions/v19/assets/A0017/
A0018 | Programmable Automation Controller (PAC) | Embedded | A Programmable Automation Controller (PAC) is an embedded programmable control device. PACs are designed to enable automation applications across integrated software applications, peer controllers (e.g., PLC), Human Machine Interfaces, and other systems. PACs often include advanced features for process control, motion control, drive control, and vision applications. PACs are programmed using traditional process automation programming languages (IEC-61131) and sometimes languages such as C and C++ to support more advanced controls. | https://attack.mitre.org/versions/v19/assets/A0018/

## Asset Technique Map
Technique ID | Technique | Asset ID | Asset | Basis
T0800 | Activate Firmware Update Mode | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0800 | Activate Firmware Update Mode | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0800 | Activate Firmware Update Mode | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0800 | Activate Firmware Update Mode | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0800 | Activate Firmware Update Mode | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0800 | Activate Firmware Update Mode | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0800 | Activate Firmware Update Mode | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0800 | Activate Firmware Update Mode | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0800 | Activate Firmware Update Mode | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0801 | Monitor Process State | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0802 | Automated Collection | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0802 | Automated Collection | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0802 | Automated Collection | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0802 | Automated Collection | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0802 | Automated Collection | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0806 | Brute Force I/O | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0806 | Brute Force I/O | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0806 | Brute Force I/O | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0806 | Brute Force I/O | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0806 | Brute Force I/O | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0806 | Brute Force I/O | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0806 | Brute Force I/O | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0806 | Brute Force I/O | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0807 | Command-Line Interface | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0807 | Command-Line Interface | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0807 | Command-Line Interface | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0807 | Command-Line Interface | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0807 | Command-Line Interface | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0807 | Command-Line Interface | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0807 | Command-Line Interface | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0807 | Command-Line Interface | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0807 | Command-Line Interface | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0809 | Data Destruction | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0811 | Data from Information Repositories | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0811 | Data from Information Repositories | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0814 | Denial of Service | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0816 | Device Restart/Shutdown | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0817 | Drive-by Compromise | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0819 | Exploit Public-Facing Application | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0819 | Exploit Public-Facing Application | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0819 | Exploit Public-Facing Application | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0819 | Exploit Public-Facing Application | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0820 | Exploitation for Evasion | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0821 | Modify Controller Tasking | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0821 | Modify Controller Tasking | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0821 | Modify Controller Tasking | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0821 | Modify Controller Tasking | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0822 | External Remote Services | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0822 | External Remote Services | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0822 | External Remote Services | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0822 | External Remote Services | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0822 | External Remote Services | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0822 | External Remote Services | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0822 | External Remote Services | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0822 | External Remote Services | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0822 | External Remote Services | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0823 | Graphical User Interface | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0823 | Graphical User Interface | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0823 | Graphical User Interface | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0823 | Graphical User Interface | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0823 | Graphical User Interface | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0823 | Graphical User Interface | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0823 | Graphical User Interface | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0823 | Graphical User Interface | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0823 | Graphical User Interface | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0830 | Adversary-in-the-Middle | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0834 | Native API | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0835 | Manipulate I/O Image | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0835 | Manipulate I/O Image | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0835 | Manipulate I/O Image | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0835 | Manipulate I/O Image | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0836 | Modify Parameter | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0836 | Modify Parameter | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0836 | Modify Parameter | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0836 | Modify Parameter | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0836 | Modify Parameter | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0838 | Modify Alarm Settings | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0838 | Modify Alarm Settings | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0838 | Modify Alarm Settings | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0838 | Modify Alarm Settings | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0838 | Modify Alarm Settings | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0838 | Modify Alarm Settings | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0838 | Modify Alarm Settings | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0838 | Modify Alarm Settings | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0840 | Network Connection Enumeration | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0842 | Network Sniffing | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843 | Program Download | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843 | Program Download | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843 | Program Download | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843 | Program Download | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.001 | Download All | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.001 | Download All | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.001 | Download All | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.001 | Download All | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.002 | Online Edit | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.002 | Online Edit | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.002 | Online Edit | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.002 | Online Edit | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.003 | Program Append | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.003 | Program Append | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.003 | Program Append | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0843.003 | Program Append | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0845 | Program Upload | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0845 | Program Upload | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0845 | Program Upload | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0845 | Program Upload | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846 | Remote System Discovery | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.001 | Port Scan | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.002 | Broadcast Discovery | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0846.003 | Multicast Discovery | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0847 | Replication Through Removable Media | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0848 | Rogue Master | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0849 | Masquerading | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0849 | Masquerading | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0849 | Masquerading | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0849 | Masquerading | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0849 | Masquerading | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0849 | Masquerading | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0849 | Masquerading | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0851 | Rootkit | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0852 | Screen Capture | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0852 | Screen Capture | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0852 | Screen Capture | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0853 | Scripting | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0853 | Scripting | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0853 | Scripting | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0853 | Scripting | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0853 | Scripting | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0853 | Scripting | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0853 | Scripting | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0853 | Scripting | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0853 | Scripting | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0858 | Change Operating Mode | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0858 | Change Operating Mode | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0858 | Change Operating Mode | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0858 | Change Operating Mode | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0859 | Valid Accounts | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0860 | Wireless Compromise | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0860 | Wireless Compromise | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0861 | Point & Tag Identification | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0862 | Supply Chain Compromise | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0863 | User Execution | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0863 | User Execution | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0863 | User Execution | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0864 | Transient Cyber Asset | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0865 | Spearphishing Attachment | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0865 | Spearphishing Attachment | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0866 | Exploitation of Remote Services | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0867 | Lateral Tool Transfer | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0867 | Lateral Tool Transfer | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0867 | Lateral Tool Transfer | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0867 | Lateral Tool Transfer | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0867 | Lateral Tool Transfer | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0867 | Lateral Tool Transfer | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0868 | Detect Operating Mode | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0868 | Detect Operating Mode | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0868 | Detect Operating Mode | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0868 | Detect Operating Mode | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0869 | Standard Application Layer Protocol | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0871 | Execution through API | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0872 | Indicator Removal on Host | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0873 | Project File Infection | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0873.001 | Siemens Project File Format | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0874 | Hooking | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0877 | I/O Image | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0877 | I/O Image | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0877 | I/O Image | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0877 | I/O Image | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0878 | Alarm Suppression | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0881 | Service Stop | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0883 | Internet Accessible Device | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0883 | Internet Accessible Device | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0883 | Internet Accessible Device | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0883 | Internet Accessible Device | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0883 | Internet Accessible Device | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0884 | Connection Proxy | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0885 | Commonly Used Port | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0886 | Remote Services | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0886 | Remote Services | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0886 | Remote Services | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0886 | Remote Services | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0886 | Remote Services | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0886 | Remote Services | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0886 | Remote Services | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0886 | Remote Services | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0886 | Remote Services | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0887 | Wireless Sniffing | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0887 | Wireless Sniffing | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0888 | Remote System Information Discovery | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0889 | Modify Program | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0889 | Modify Program | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0889 | Modify Program | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0889 | Modify Program | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0890 | Exploitation for Privilege Escalation | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0892 | Change Credential | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0893 | Data from Local System | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0893 | Data from Local System | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0893 | Data from Local System | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0893 | Data from Local System | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0893 | Data from Local System | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0893 | Data from Local System | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0893 | Data from Local System | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0893 | Data from Local System | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0894 | System Binary Proxy Execution | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0894 | System Binary Proxy Execution | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0894 | System Binary Proxy Execution | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0894 | System Binary Proxy Execution | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0894 | System Binary Proxy Execution | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0894 | System Binary Proxy Execution | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0895 | Autorun Image | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0895 | Autorun Image | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0895 | Autorun Image | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0895 | Autorun Image | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0895 | Autorun Image | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T0895 | Autorun Image | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691 | Block Operational Technology Message | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691 | Block Operational Technology Message | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691 | Block Operational Technology Message | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691 | Block Operational Technology Message | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691 | Block Operational Technology Message | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691 | Block Operational Technology Message | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691 | Block Operational Technology Message | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691 | Block Operational Technology Message | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691 | Block Operational Technology Message | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.001 | Command Message | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.001 | Command Message | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.001 | Command Message | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.001 | Command Message | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.001 | Command Message | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.001 | Command Message | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.001 | Command Message | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.001 | Command Message | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.001 | Command Message | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1691.002 | Reporting Message | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692 | Unauthorized Message | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692 | Unauthorized Message | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692 | Unauthorized Message | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692 | Unauthorized Message | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692 | Unauthorized Message | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692 | Unauthorized Message | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692 | Unauthorized Message | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692 | Unauthorized Message | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.001 | Command Message | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.001 | Command Message | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.001 | Command Message | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.001 | Command Message | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.001 | Command Message | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.001 | Command Message | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.001 | Command Message | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.001 | Command Message | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.002 | Reporting Message | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.002 | Reporting Message | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.002 | Reporting Message | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.002 | Reporting Message | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.002 | Reporting Message | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.002 | Reporting Message | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.002 | Reporting Message | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.002 | Reporting Message | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1692.002 | Reporting Message | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693 | Modify Firmware | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693 | Modify Firmware | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693 | Modify Firmware | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693 | Modify Firmware | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.001 | System Firmware | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.002 | Module Firmware | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.002 | Module Firmware | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.002 | Module Firmware | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1693.002 | Module Firmware | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694 | Insecure Credentials | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.001 | Default Credentials | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1694.002 | Hardcoded Credentials | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695 | Block Communications | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.001 | Serial COM | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.002 | Ethernet | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0001 | Workstation | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0002 | Human-Machine Interface (HMI) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0003 | Programmable Logic Controller (PLC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0004 | Remote Terminal Unit (RTU) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0005 | Intelligent Electronic Device (IED) | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0006 | Data Historian | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0007 | Control Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0008 | Application Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0009 | Data Gateway | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0010 | Safety Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0011 | Virtual Private Network (VPN) Server | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0012 | Jump Host | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0013 | Field I/O | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0014 | Routers | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0015 | Switch | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0016 | Firewall | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0017 | Distributed Control System (DCS) Controller | Direct active MITRE targets relationship; not model-specific vulnerability evidence
T1695.003 | Wi-Fi | A0018 | Programmable Automation Controller (PAC) | Direct active MITRE targets relationship; not model-specific vulnerability evidence

## Provenance
Field | Value
version | 19.2
sourceUrl | https://raw.githubusercontent.com/mitre-attack/attack-stix-data/c2494b29dd268c46a5d0ea0990553e4327cd2253/ics-attack/ics-attack-19.2.json
repositoryCommit | c2494b29dd268c46a5d0ea0990553e4327cd2253
sha256 | 08b83d2cea6b6d6752468ef0e62e2ab2a53c9443ef72c439ecccb07ab9e89da9
sourceBytes | 4057891
retrievedAt | 2026-11-01T21:43:50+00:00
indexUrl | https://raw.githubusercontent.com/mitre-attack/attack-stix-data/c2494b29dd268c46a5d0ea0990553e4327cd2253/index.json
indexSha256 | c2a0a71ffc6f0242e7ea00cbac0fe64bc71d8415b21af05b8424d409bd562d7f
licenseUrl | https://raw.githubusercontent.com/mitre-attack/attack-stix-data/c2494b29dd268c46a5d0ea0990553e4327cd2253/LICENSE.txt
licenseSha256 | 738144f7fb054722a4ef9d3367c51710341dc12fc574c6ac3a41daaaecd8bf5e
transformVersion | 1.0.0
websiteVerified | False
webSources | [{'view': 'ICS', 'url': 'https://attack.mitre.org/versions/v19/matrices/ics/', 'sha256': '35998962584667c2814718287b2052c5c891c07cf3bd5cfe63e5ed6ab13bb21f', 'retrievedAt': '2026-11-01T21:43:50+00:00'}]
unavailableWebViews | [{'view': 'Embedded', 'url': 'https://attack.mitre.org/versions/v19/matrices/ics/embedded/', 'httpStatus': 404, 'retrievedAt': '2026-11-01T21:43:50+00:00'}, {'view': 'Windows', 'url': 'https://attack.mitre.org/versions/v19/matrices/ics/windows/', 'httpStatus': 404, 'retrievedAt': '2026-11-01T21:43:50+00:00'}, {'view': 'Linux', 'url': 'https://attack.mitre.org/versions/v19/matrices/ics/linux/', 'httpStatus': 404, 'retrievedAt': '2026-11-01T21:43:50+00:00'}, {'view': 'Network Devices', 'url': 'https://attack.mitre.org/versions/v19/matrices/ics/network-devices/', 'httpStatus': 404, 'retrievedAt': '2026-11-01T21:43:50+00:00'}]

## License
MITRE license and disclaimers — retained verbatim
License
-------
The MITRE Corporation (MITRE) hereby grants you a non-exclusive, royalty-free license to use ATT&CK® for research,
development, and commercial purposes. Any copy you make for such purposes is authorized provided that you reproduce
MITRE's copyright designation and this license in any such copy.
"© 2026 The MITRE Corporation. This work is reproduced and distributed with the permission of The MITRE Corporation."
Disclaimers
-----------
MITRE does not claim ATT&CK enumerates all possibilities for the types of actions and behaviors documented as part
of its adversary model and framework of techniques. Using the information contained within ATT&CK to address or cover
full categories of techniques will not guarantee full defensive coverage as there may be undisclosed techniques or
variations on existing techniques not documented by ATT&CK.
ALL DOCUMENTS AND THE INFORMATION CONTAINED THEREIN ARE PROVIDED ON AN "AS IS" BASIS AND THE CONTRIBUTOR, THE
ORGANIZATION HE/SHE REPRESENTS OR IS SPONSORED BY (IF ANY), THE MITRE CORPORATION, ITS BOARD OF TRUSTEES, OFFICERS,
AGENTS, AND EMPLOYEES, DISCLAIM ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT
THE USE OF THE INFORMATION THEREIN WILL NOT INFRINGE ANY RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR
FITNESS FOR A PARTICULAR PURPOSE.